# VOLUME 3

# TECHNICAL SPECIFICATIONS

TECHNICAL DESCRIPTION

The installation of public and decorative lighting is the property of Plandište municipality, and municipality finance maintenance of public lighting from budget funds.
 An analysis of the current situation was done. A list of public lighting with the basic data on the number and type of poles and luminaires, as well as installed capacity is made. 
The analysis noted the poor condition of poles and luminaires, and the total bills for the electricity consumed for public lighting indicate, that in the coming period, it is necessary to complete the reconstruction of public and decorative lighting.

Based on the analysis it was suggested that public lighting in the central city streets should be completely reconstructed (along with the reconstruction of roads), and in other streets the existing light  sources  just to be replaced with new sources on existing poles.

In the main streets: Vojvode Putnika, Karađorđeva and Hajduk Veljkova, completely new public lighting is designed.

Lighting of these streets, parking lots, pedestrian and bicycle paths is designed according to regulations and environmental requirements. Luminaires with LED sources, power 106W or 75W, with the possibility of regulation in the range of 30% to 100% are selected. The luminaires are mounted on metal poles height of 4m or 8m.

In other streets of Plandište city (24 streets) is recorded a total of 360poles, and the height of the poles is 6 to12m, except Saša Jorgovan Square where the poles are 3m height. Existing light sources are mercury lamps with installed capacity of 125W.These lamps will be replaced by lamps with LED light modules, power 75W.

LED light sources are characterized by high luminous efficiency, which as a result has significantly reduced power consumption compared to conventional light sources.

All  proposed luminaires have the dimming option-reduction of luminous flux, and therefore  the power are adjustment to the desired value in the late evening hours, which is important from the standpoint of energy efficiency.

Proposed mode with dimming achieves additional electricity savings of about 27%.

Long service life of LED light sources (50,000 - 100,000 hours) is several times higher compared to other sources, which drastically reduces the need for maintenance during operation of such an installation.

It is designed remote control system which allows remote diagnostics with the ability to manage, i.e. turning on and off lights, as well as the dimming. This is a system that allows two-way communication, respectively has the ability to send commands as well as to receive information on the current status of the lights, as well as confirmation that the command is executed. Thanks to the two-way communication between the lamp and the control (directing) centre, it is possible to detect lamps malfunction or damage or a power supply problem by the operator.

The remote control includes the collection, use, and processing of data on the work of public lighting system, and lately use of these data in order to further regulation.

The system consists of three main elements: the lights controller (in each new luminaire), remote control systems in distribution cabinets (in 3 new ROJO) and management software. The system allows full control of installation of public lighting and in every moment provides a complete insight into its work. By entering a user page (web page that requires a user name and password), it is possible to obtain information about each luminaire (the possible failure on one of the components - light bulbs, electronic ballast or controller , the time of inclusion and exclusion of the consumption of electricity). Also, it is possible to control the luminous flux or power, depending on the actual needs confirmed by photometrical calculation (as a function of aging sources CLO (Constant Lumen Output) or oversized installations VPO (Virtual Power Output). By defining alarms for specific users of the system which determines the investor (creating new user names and passwords), it is possible to get information via e-mail or text messages about the performance of each lamp and complete installation. The system is open - users can access the system from any computer or smart phone and check the status or make changes to the installation (dimming or turning on / off certain lights in case you need to check the work). To access the system it is necessary that the user creates the appropriate user name and password, otherwise the access is not possible (adequate protection system at all levels - user access to the server with a user name and password  through a secure https protocol, the connection between the server and the remote control systems in distribution cabinets realizes safe VPN connection. Also, it is possible to arrange lamps in different  groups if required a certain time lamps are in different operating modes. During the year, the length of the night changes, and the script of the installation can be adapted to any change (thus avoiding unnecessary costs when installation works longer than necessary or lamps not include when necessary).

System for remote management and control of public lighting (i.e. the telemanagement) is conceived as a network system with several levels of command .The core of the system is a server (the computer on which the data base is located) placed in the cloud or control centre and associated with one or more PCs that are used for system management. Server has application software responsible for managing the entire system, the collection, analysis and data processing. Using this system operator can simultaneously manage multiple systems of public lighting through sectional controllers which are usually placed in the power distribution boards. Communication server, i.e. Link between management centre and sectional controllers in control cabinets is bidirectional and takes place over TCP/ IP protocols (GPS, GPRS, Edge, 3G /4G, DSL (ADSL) technology, as well as existing LANs).

Remote control systems in distribution cabinets (same as definition ,,Segment controller’’)  is responsible for communication between the server and light's controller,   the connection is realized through two way comminucation. Segment controller can control up to 150 group of lights (nodes).  System has independent power supply, it can stand out so it has IP66 or can have separate waterproof housing. Luminaires controller communicates with driver which can operate and follow the commands from controller via DALI or 1-10V. The device is equipped with a measuring device class 1 (measurement error is less than 1% in the entire power range), and continuously measure and monitor: current, voltage and power factor of luminaires. The device maintains all settings even in case of interruption of communication with devices of higher priority. It has a built-in astronomical clock which allows switching on and off the lamp. There is possibility to connect different sensors. The device can connect various sensors (photocells, detector movement). User interface is located on the server which could be located anywhere (open system). Server can be accessed through some of the IP connection: 3G/4G mobile network, or via EDGE or GPRS technology, via Ethernet or Wi-Fi communication accessing the appropriate Web site and registration (WAN or LAN address).On this way you can locate and monitor the installation of lighting, even over the map provided by Google Map service, configure the system, change the scenario set or shutting down lights plan and all this on the Web page of the system. All collected data is stored and kept in a SQL database, making the information available for a longer period of time, primarily for the analysis of electricity consumption, prediction lifetime of the light source, detection of problems.