# VOLUME 3

# TECHNICAL SPECIFICATIONS

Adaptation and rehabilitation of the old Psychiatry building in No. 51 Knez Mihajlova Street in Smederevo

1. CONSTRUCTION WORKS

The existing condition of the building:

The building has a monumental property significance, has a status of a property under previous protection and is covered by the Plan for the Protection of Immovable Cultural Property. Taking into consideration the duration and purpose of the building, the original art and architecture of the building is preserved to a great extent. For many years, it has not thoroughly been invested in the protection of the facility in terms of protection against moisture and therefore from the aspect of the static stability of the bearing structure, a certain professional investigation should be carried out.

The concept of adaptation and rehabilitation:

The building must be repaired from the harmful moisture and the constructive system must be consolidated as a whole. Consequently, the rehabilitation and revitalization of facade panels should be carried out in accordance with their original properties and architectural values.

Facade works and rehabilitation of surfaces with moisture problems:

On the building, as a whole, the effects of harmful moisture on façade and partition walls can be noticed. The mortar is bubbled and fell off the parts of the plinth from the outside of the building, and on the parts of the internal partition walls, the moisture penetration of up to 1.5m height on certain walls is noticed. In one wing of the building, almost daily maintenance works have been carried out so that no moisture effect can be seen and is currently not noticeable.

It is necessary to have the complete facade mortar of the whole building stripped off to the brick, clean the joints and re-mortar with the flexible mortar, while retaining the decorative shapes using the templates based on the prints previously taken on the facade itself. The finishing of the facade is to be made of bavalite and with rough processing.

In the interior walls, stripping off the mortar of up to a height of 1.5 m is planned with re-plastering with mortar afterwards.

Taking into consideration that moisture also affects the stability of the structure, it is necessary to perform the moisture cutting off using modern materials and thus prevent the process from spreading vertically. For the reparation of the walls, we suggest stripping off the mortar where the walls will be cut by the machines, the cuts of 8-10mm thickness and 10-20cm of height. A bitumen tape with a polyester felt insert is to be put in cuts, with flexible mortar of certain density, together with hydro insulation that overlaps 5-7cm. Previously use wooden pins to support the walls in order to prevent the subsidence of the object. The position of the wall cut is to be defined above the level of the finished floors by 5cm. There is no visible penetration of moisture on the floors, considering the type of the floor coverings that were laid( vinflex, ceramics) but the floor surfaces need to be protected against the moisture as well as thermally insulated with a hard layer of insulating material with a reinforced cement overcoat.

Works on the lowered ceiling:

The construction of a 9.5mm suspended ceiling plasterboard with a suitable grid of aluminum UD and CD profiles, hangers and all the connecting and other necessary materials is planned for the whole building. The suspended ceiling will be installed hanging from the attic structure at the height of 3.50m measured from the floor. In the rooms where moisture is detected, as in sanitary blocks, the waterproof plaster boards are to be installed.

Works on the floor coverings:

The existing floors are made either of ceramic or vinflex, which are mostly damaged. Due to the necessary hydro and thermal insulation of the floors, new floors of good quality granite ceramics are needed over the insulating layers.

Works on the wall treatment:

All wall surfaces should be prepared, the blown mortar taken off, re-plastered and painted with acrylic paint.

Works on the replacement of joinery:

The facade joinery has been greatly worn out and should be replaced with a new PVC five-chamber carpentry with curtains - venetian blinds, against the sun. The position, dimensions and geometric appearance of the carpentry should not be changed, as given in the carpentry schemes within the project. The roof windows are to be kept in the same position and of the same dimensions and shape.

The interior carpentry was also worn out and should be replaced with a new wooden one with MDF filling, and the high partition elements should be shortened to the height of the lowered ceiling.

Repair works on the roof and roof covering:

The roof is designed as a multi-level one with a roof structure of the real king post and which is in solid condition so that only partial replacement of wooden structural elements is planned. The roof cover is a double pepper tile, which should be completely replaced. When replacing the structure, cover the roof deck with 2.5 cm planks, place the aluminum foil and replace the battens by installing completely new ones – longitudinal for ventilation of the roof and transverse for carrying the tiles. The roof cover is a double crown tile, which has evidently much deteriorated and should be completely replaced. Gutters are made of galvanized sheets, laid horizontally and should be completely replaced. The tilting verticals are also made of galvanized sheets and their replacement should be planned. Roofing liners on valleys, fire walls, around roof windows, as well as at the connection points of the lying gutters with the grips should be replaced with a galvanized sheet of 0.55mm thickness of the developed width in accordance with the detailing.

Heating installations:

The heating was installed quite a long time, so we planned the complete replacement of the pipe network and heating units in accordance with the purpose of the premises.

Electrical installations:

The electrical installations are worn out and a complete replacement is considered in accordance with the regulations and purpose of the facility.

Water and sewer installations:

Complete installation of water supply and sewerage should be done in accordance with the new purpose of the rooms and installation of necessary sanitary facilities and sanitary blocks equipment.

Protection of the object against atmospheric influences:

Atmospheric waters are collected from the roof surfaces by gutters and gutter verticals which bring the water to the green areas by the drain flumes or by connecting into a closed system to the atmospheric sewage in the immediate environment. Around the whole building, a sidewalk of 1,00m width with a 1% cross-sectional slope from the building should be made so that the atmospheric water is rejected from the ground. In some of the parts around the building, the staircase groups are to be constructed to overcome the denivelation of the field, as well as providing ramps for handicapped people in front of all the entrances to the building.

2. HEATING

The project should plan for the dismantling of existing, old central heating installations, installations and equipment faults diagnosis, then the selection of installations and equipment to be used and the unusable equipment removed. As the installation and equipment are very old, it is necessary to make replacement of the complete installation and armature reinforcement mesh,.

Primary fluid hot water 90/70 (оC) from the existing boiler room "Hospital" with forced circulation.

The location and method of connection to the heating system as well as the check of the consumers has been determined (the heating system was brought to the building and replaced due to a pipe perforation a year ago) so that the heating system and the substation are not included in the project.

The heat loss calculation is to be made at the outside project temperature for Smederevo of t s = -12.1 оC.

The heat transfer coefficient is calculated and determined based on the existing project documentation and the condition of the facility.

For heating elements, the aluminum radiators shall be approved with the required power and length, and in accordance with the possibilities of assembly on site. The pipe network should be constructed of black steel tubes, and in the facility they should be implemented to meet the best technical and aesthetic solutions. Either ventilation valves on each heating unit should be provided or the central ventilation of the system at the highest point of the facility.

Connecting the heating system to the heating source, as well as the expansion solution is not an objective of this project.

Using the data of the new architectural and construction solution of the health facility, the ventilation of the rooms is not necessary.

Note: The existing building has radiator heating from the Hospital boiler room (housed in a separate facility). The heating units are mostly old Russian radiators, and there are about 30% of the old Jugoterm radiators.

3. WATER SUPPLY  AND SEWAGE SYSTEM

Water supply

Based on the architectural solution of the adaptation of the facility, the sanitary facilities are planned for the functional performance of the planned activity. The sanitary water supply was designed based on the layout of sanitary facilities. The connection is provided on the line which is parallel to Knez Mihailova Street, and the hydraulic calculation showed that PE pipe ND 32, NP of 6 bar is sufficient for the connection. The main distribution of the sanitary water is under the floor of the building and runs in 3 directions through the PE pipes ND32 / 6. The pipes distribution branching under the floor of the building to the walls on which the fittings and sanitary facilities are installed is also made of the PE pipe of the nominal diameter ND20 / 6 (20mm is the outer diameter of the PE pipe). The branching distribution above the floor is made of polypropylene pipes (PP pipes) for the pressure of 6 bar. The indicated diameters in the isometric scheme are the inner diameters of these tubes.

Sewage system

On the part of the building towards the Petrijevski potok Street, the reconstruction of the sewerage diversion was carried out last year and the main drain was constructed of D160mm PVC pipes into the revision manhole located in the green area next to the Petrijevski potok street, from which it was later brought to a faecal collecting facility beneath this street. The sewerage in the remaining part of the building has not been reconstructed and occasional floor leaks are noticed. This documentation provides for a new PVC pipe distribution, with 5 ventilation vertices, where the revision openings are planned to be located above the floor of the building. This new distribution branching is shown at the base of the facility. It is connected to the reconstructed part and goes towards the collector facility in Petrijevski potok Street.

Laying of installations under the floor requires cutting the existing concrete liner together with breaking and removal of the debris. After the installations are set, the floor is to be concreted over the trench. The wall installations are beneath the wall coatings, except for the ventilation verticals, which are masked.

4 ELECTRICAL INSTALLATION

This contract should address the following:

- a new power cable for the psychiatric building from the hospital's electrical distribution cabinet to the new KPO

- main electrical distribution cabinet

- required distribution boards

- electrical installation of lighting and sockets in all rooms with distribution boards

- grounding and lightning installation

- necessary (panic) lighting

- TT installation in the facility

- Intercom installation

- Install video surveillance