# VOLUME 3

# TECHNICAL SPECIFICATIONS

CONTENT

Page

1. INVESTMENT AND ENGINEERING.........................................................................	3

1.1 Existing condition..........................................................................................................	3

1.2. Desired condition ...................................................... ............................... ..................	3

2. HYDRO TECHNICAL INSTALLATIONS ............................... ..................................	4

2.1 Water supply............................... ............................... ............................... ..................	4

2.2. Sewerage............................... ............................... ............................... .......................	4

2.3. Sanitary fittings............................... ............................... ............................... .............	5

2.4. General remarks............................... ............................... .............................................	5

3. ELECTRO-TECHNICAL INSTALLATIONS............................... ............................... 	5

3.1. Dimensioning of cables............................... ............................... ...............................	6

3.2. Installation of lighting............................... ............................... ...............................	7

3.3. Installation of electric sockets............................... ............................... .......................	7

3.4. Protection from electric shock............................... ............................... ......................	7

3.5. Installation of structural cabling and telephone............................... ...........................	8

1. INVESTMENT AND ENGINEERING

1.1 Existing condition

Adaptation relates to a part of existing facility of Health Centre. This part includes two medical premises, sanitary block and a part of the hall. Net surface area is 134,92 m2.

The structure of the facility i massive system with block walls, with vertical and horizontal ring beams of reinforced concrete.  Circumferential walls are of a sandwich type and internal bearing walls are built in full brick d=25 cm. Partition walls are of brick 12 cm.

Floor slabs structure is of a rib-type  *TM-3*,  20 cm thick.

Interior height of premises is 345 cm, measured from the floor to the finished ceiling.

Exterior joinery is wooden.

Interior finishing works are done in the following manner:

- plastered, skimmed and painted room walls in semi-dispersive paint or coated with tiles up to required height as appropriate.  Floors covered in ceramic tiles.

-  joinery (interior doors) are doors with plywood on both sides, (solid with transom) with wooden frames

The facility is equipped with necessary installations due to the purpose of the building:

-    lighting and fitting

ventilation of the facility is natural through windows

sanitary equipment and water supply in sanitary blocks are supplied with water from water supply system

heating through radiators connected in system of central (level) heating

1.2. Desired condition

Current structure and organisation of space is basically preserved (position of sanitary block, hall...). Due to the requirements of ophthalmological service it is necessary to split the existing medical premise to four inter-connected rooms which will fulfil their requirements. Partitioning is done by the walls of plaster slabs with thermal insulation of mineral wool.  In these newly designed rooms suspended ceiling is to be made of plaster slabs. This way the sewerage network elements from upper floor, under the ceiling, are covered.

The other medical room will be turned to conference room for the staff and for education of patients. The room will be equipped by all required technical equipment. Capacity is 41 seats in the audience.

Existing sanitary block remains with the same layout, but one anteroom will be turned in changing room for the staff from which the access to sanitary block for the staff is provided. The other sanitary block will be for the patients.

In the respective part of the hall chairs will be placed for the patients since this part of the hall is also a waiting room. .

All existing floor covers in relevant premises (except the respective part of the hall) need to be removed. Except in sanitary block (where ceramic tiles are foreseen) and the respective part of the hall (where current floor coating is preserved) in all other premises granite ceramic tiles will be laid.  Parts of walls in newly designed infirmaries in sanitary zones around the wash basins will be covered in ceramic tiles. Also, existing ceramic tiles on the walls of sanitary blocks and around the current sink will be removed and replaced with new ceramic tiles.

Current wall surfaces and ceilings, and surfaces of partition wall of plaster slab and suspended ceiling will be skimmed and primed with high quality antibacterial low maintenance layer recommended for medical premises.

All existing wooden exterior joinery (windows) and interior in respective premises will be replaced with new PVC joinery glazed with low-emission glass. New exterior joinery should be done according to existing one (observe the proportion of fields and wings) in order not to disturb the exterior looks of the building. Striped curtains will be supplied to all the windows except in sanitary blocks. Because of the nature of ophthalmological exam it is necessary to provide for occasional complete darkening of rooms, therefore roll blinds are foreseen with the screen canvas.

Interior joinery – doors should be according to the model of existing ones (with transoms up to the ceiling to be glazed with transparent or matt glass, depending on the position and purpose of the room).

For the space in question new equipment is foreseen / mobile fittings such as desks, appropriate types of chairs and stools, cabinets, bed, kitchenette cabinet elements. All sanitary elements – wash basins, sink, WC and shower baths will be replaced with new ones of better quality.

2. HYDRO TECHNICAL INSTALLATIONS

Adaptation relates to a part of existing facility of Health Centre. This part includes two medical premises, sanitary block and a part of the hall.

The facility in question is equipped with necessary installations of water supply and sewerage in line with the purpose of the building. In medical room 1 there is a tap / sink as well as in the adjacent room which is not a part of the space in question. Having regard to the fact that the room No. 1 will be split in four rooms two of which, infirmaries, will have to be equipped with taps /wash basins, it is required to lead the water from the nearest existing taps and connect new outlets to existing ones.

Survey on the spot should reveal how the new installation will be adapted to existing one.

2.1 Water supply

The facility of Health Centre is connected to existing water supply on the stretch.

Water supply network which needs to be upgraded will be done of PVC water supply pipes and purpose-made parts of appropriate diameter with fixtures of individual parts by screwing and applying fine hemp soaked in linen seed oil. Stop valve is to be built-in at each new tap.

Hot water in sanitary block will be provided from an electric boiler of 80 l placed in changing room for the staff. From there the pipe will be led alongside the walls to the wash basin and showers. Hot water pipe shall be wrapped in corrugated paper so as to avoid damage to the walls, wall lining and pipes during temperature expansions, and to prevent water cooling.

2.2. Sewerage

The building is connected to existing outlet on the stretch.

Due to other premises of the facility being in function, and the fact that adaptation of the space in question may not disturb the functioning of other spaces, it is necessary to do a careful survey of the condition of installations in the space in question and connect new parts of sewerage network through the simplest and shortest route to existing network.

All the new ducts of sewerage network will be done by PVC sewerage pipes joined by couplings with rubber seals.

2.3. Sanitary fittings

Sanitary fitting is fixed through the siphon. In front of a sanitary fitting there is appropriate stop valve with galvanised cap. Sanitary fitting is of standard manufacturing, standard dimensions in colour as decided by client, with all respective reinforcement and other equipment required for assembly and proper functioning.

Relevant space contains the following sanitary fittings:

2 WC with highly placed flushing cistern

4 wash basins with standing taps and mirrors (two in sanitary block and two in infirmaries)

2 shower cabins

2.4. General remarks

- rough works are to be done according to descriptions in the Priced bill of quantities observing all regulations in the field of protection at work;

- all the pipes, valves and joining material should be carefully checked before installation for possible flaws;

- obtain type approval certificate for all built-in materials;

- all opening for leading the pipes through should be restored in accordance with the surface around them;

- all the works have to be done in compliance with technical regulations and instructions of competent authorities.

3. ELECTRO-TECHNICAL INSTALLATIONS

This chapter foresees the following electric installations  in compliance with the tasks and requests of the client:

- distribution cabinet (RO-OF) for electricity supply

- interior installations of general electric lighting

- installations ,,panic” for lighting on exits and halls

- installation of mono-phase earthed sockets and connections

- installations for equalising potentials and

- Installations of structural cables and telephone.

For electricity supply of newly-designed electric installations, in addition to existing RO, installation of new polyethylene distribution cabinet RO – OF is foreseen, of standard manufacturing, in PVC housing, for incorporation in the wall. The cabinet is meant for three-phase connection (L1, L2, L3, N and PE) from OMM. Distribution cabinets are connected over existing OMM to distribution network NN in line with requirements of responsible Distributor of Electric energy.

Technical solutions foreseen by this design are in compliance with standards SRPS, IEC and ISO in force, other technical regulations for this field and best engineering practice.

Designed installations are not foreseen for connecting large consumers for heating premises, since a separate heating is installed in the facility running on other type of power source.

General properties and classification of external impacts

Properties of supply sources are 3×230/400V, 50Hz. Electric supply system when it comes to earthing is TN-C/S. Installed and maximal electric power is marked on the one-pole scheme.

In respect of environment impact, (SRPS N.B2.730) the facility has the following impact classes:

- temperature AA4

- elevation, AC1

- presence of water, AD1

- presence of external hard materials, AF1

- mechanical stress, AG1

- vibrations, AH1

- presence of flora AK 1

- presence of fauna AL1

- electromagnetic and electrostatic impact AM1

- solar radiation AN1

- seismic effects AP1

- lightning AQ1

- In respect of utilisation, the designed facility is classified in the following classes:

- qualified persons BA1

- electric resistance of human body BB1

- contact of person with earth potential BC2

- possibilities for evacuation BD1

- nature of processed material BE1

- In respect of structure, the facility is classified in following classes:

- composition of material CA1

- facility structure CB1

Based on previously done classification of external impacts, appropriate equipment is selected in compliance with requirements of SRPS N.B2.751 and electric distribution is done according to SRPS N.B2.752.

3.1. Dimensioning of cables

Selection of cross cuts of cables is done on the basis of permanently permitted currents in compliance with SRPS N.B2.752  and SRPS N.B2.752/1. Cables for interior installations in the facility are laid in the wall underneath plaster, according to the mentioned standard it is the type C.

Temperature of the ambient where cables are laid corresponds to those temperatures for which SRPS prescribes permanently permitted currents (for cables laid in earth 200C, and for the cables in the air 300C), thus the adopted temperature corrective factor is kt=1.

For the case of parallel laying of up to 6 current circuits in a group (embedded or closed cables) the standard provides for corrective factor of kn=0,55, in the worst case if all the cables were to be simultaneously loaded with permanently permitted currents long enough to reach the temperatures of stationary condition. Since permanently permitted currents of adopted cables are far higher than the actual currents of loading, a correction factor is adopted for group current circuits of kn = 0,85.

Permanently permitted currents of adopted cables, depending on the type of separation, type of insulation and adopted correction factors meet the conditions of SRPS N.B2.743 and  SRPS N.B2.743/1.

3.2. Installation of lighting

For lighting of premises appropriate installation is foreseen of light bulbs with lamps. Lighting installation is done by cables of type N2XH 2,3×1,5 mm2, partly in the wall, underneath plaster.

Switching on of lighting is done with appropriate single-pole installation switch placed in the wall, installed next to doors, on the side where the lock is, at the height of h=1,5m.

For panic lighting of evacuation routes and exits luminaires are foreseen with own supply source (Ni-Cd batteries), automatic refill and automatic switch on in case of network power cut. Installation of panic lighting provides the passage through communications to exit from the building, in case of evacuation and voltage dropping and they should be supplied with labels indicating the direction of movement towards the nearest exit.

3.3. Installation of electric sockets

In compliance with design specifications and client’s request, necessary number of mono-phase earthed sockets is foreseen for equipment (interior units of SPLIT system). Sockets are selected and fixed in accordance with conditions of environment and spot where they are fixed.

In the area of infirmaries and conference room double mono-phase earthed sockets are envisaged 1 x 16A, on the wall at the height of  h = 0,5m from the level of the floor. Mono-phase sockets for air conditioner are at the height of h = 2,8 m from the finished floor level.  Sockets in kitchenette are placed above the working board of the lower cabinet at the height of 1,2 m from the level of finished floor. Sockets for electric hot plate and refrigerator are at the height of 0,6 m from the finished floor level. Sockets for 10 l boilers are placed at the height of 1,5 m from finished floor level. Attention to be paid to spacing of sockets in relation to active taps in kitchenette and infirmaries of min. 0,6 m.

Electric installations distribution for the purpose of installing mono-phase sockets is foreseen to be done by cables type N2XH 3 × 2,5 mm2, laid on the wall beneath the plaster.

3.4. Protection from electric shock

The system of electric supply with regard to earthing (JUS N. B2.730) is the TN-C-S. The function of neutral and protective conductor is unified only in a part of the system up to main points of supply , while it is farther separated in entire installation. All the installed equipment must comply with standard of direct touch protection SRPS N.B2.741 and other relevant standards for this type of equipment.

Protection from electric shock is foreseen by automatic supply switching off in case of failure, by means of provided protection appliances of differential current ZUDS according to SRPS N.B2.741. Earthing rod is the existing one, installed in the foundation of the facility  made of galvanized strip Fe-Zn 25x4mm, led through to the main point to earthing GPU, in type approved box with bus bar placed under the OMM.

Main equalization of potentials is foreseen to be done by connecting of all metal masses of non-electric installations at the facility entrance, by means of conductor P-Y 1×16 mm2 and appropriate binding material. In sanitary rooms, shower rooms, installation for equalization of potentials is foreseen by means of connecting all metal masses to PE bus bar by the box of certain type PS -49 and appropriate binding material.

In the rooms with shower additional equalizing of potentials is done by connecting simultaneously available metal masses to the box for equalizing the potentials (PS-49), by conductor PY-1x4 mm2, in PVC pipe of interior diameter  of 16 mm, in the wall, underneath the plaster. The box for equalizing potentials is connected to protection bus bar RO-OF with conductor of the type: PY-1x6mm2, in PVC pipe of interior diameter 16 mm, in the wall underneath the plaster. The box for equalizing potentials is installed in the wall at 0,2 m from the floor level at points designated in the design. Connection at shower bath should be done by cable footings and a screw M6 with a nut, and to pipeline by a clout of Fe-Zn 25x4mm stripe, lead base 24 x 3 mm along the entire length between the clout and the pipe, by cable footings and a screw with nut, and toothed washers. The manner of equalizing the potentials   in rooms with bath or shower is given in enclosed detailed design.

Contractor shall, after completing the works, measure the resistance of earthing, resistance of loop, and check the continuity of protection connector at all protected current circuits and check equal potentiality.

3.5. Installation of structural cabling and telephone

For the purpose of connecting personal computers and telephone installation, in the part of the facility that undergoes the adaptation it is required to make connections to existing local computer network, done with structural cabling of category 5E.

All connections are interconnected into a network through connectors with display RJ-45 Cat6. Cables are laid in PVC rib shaped flexible installation pipes of appropriate diameter (depending on number of cables).

Socket boxes are set at the height of 0,5 m from the finished floor level, i.e. at the level of energy sockets.

All distribution connections are done in PVC flexible self-extinguishable pipes, set at cca 20 cm above energy distribution spot.

Number of socket spots is 9.

Main distribution cabinet HD (switchboard of structural network - RACK cabinet) is existing and placed on the second floor of the facility.

Parity cables with copper conductors are installed, of category 5E, type FTP - 4x2x0,5mm2, led through rib shaped, PVC, flexible, installation pipes.

Computer network is completely done in compliance with international standard ISO/IEC

11801 2nd edition for structural cabling, and with ANSI/TIA/EIA-568-B.1 system b for linking the connector to the cable.

When preparing engineering documents, regulations used governing this field are:

- Law on Construction of buildings (Official Gazette of RS 44/95 and 16/97);

- Law on Protection at Work (Official Gazette of RS 42/91);

- International Standards ISO/IEC 11801, ANSI/TIA/EIA-568-A, IEEE 802.3, IEEE 802.4 i

- IEEE 1118;

- ITU-T recommendations concerning transfer of data, multimedia services and optical transmission.

Contractor shall, before any works begin, spot all the places where occurrence of electromagnetic interference is expected, and avoid these adjusting the routes of cable distribution and observing defined spacing.

Contractor shall, after completing the works, ensure that authorized enterprise does the measuring of earthing resistance by checking the continuity of protection conductor at all protected current circuits i.e. earthed connection parts and by checking of ZUDS worthiness to establish protection efficiency from electric shock, as well as to carry out visual check of completed installations and to issue appropriate report on expert finding.