# VOLUME 3

# TECHNICAL SPECIFICATIONS

1. SUMMARY TECHNICAL DESCRIPTION

Location of object:

The object is located in Srpska Crnja, on cad.parc.no. 7212/1 k.o. Srpska Crnja.

The object was built at a distance of 31.13 m from the regulation line.

Total area of cadastral parcel no. 7212/1 к.о. Srpska Crnja is 8408 m2.

The occupancy rate of the parcel is 12.38% and the index of construction is 0.126

Organizational design of the object:

The dimensions of the object-surveyed situation  is 33.0m x 13.40m

The dimensions of the object-projected situation with thermal insulation is 33,10m x 13,40m

Gross area of ground floor with thermal insulation p = 445,19 m2

Net area of the ground floor p = 365,54 m2

Description of the existing situation

The existing auxiliary object is a building about 60 years old, which has not been in operation for a long time. The building is due to long-lasting dysfunction, and without the necessary maintenance completely worn out. The purpose of the design is to convert the building into a temporary stay of cyclists who will pass through a path that is foreseen by international projects across Europe. In that sense, there is a need for cyclists’ accommodation. The existing contents of the building correspond almost entirely to the future requirements.

In accordance with the current legislation that defines the energy characteristics of buildings, the reconstruction and adaptation, as well as the energy rehabilitation of the building, have begun. In this sense it is necessary to perform works on the internal and external sanitation of walls, floors, ceilings and all openings. At the same time, it is anticipated the reconstruction of the complete installation water and sewage systems, as well as electrical installations and lightning installations.

The auxiliary object is made of old format bricks, with foundation made of bricks and with an inter- floor structure made of wooden roof beams with mud filling.

The roof structure is wooden and the roof is covered by clay pantiles. Wooden roof construction is curved in some places. Floors in the building are mostly made of soil.

In some places, the roof cover was damaged to such an extent that the atmospheric water penetrated the filling of wooden roof beams so that the same water flows into the rooms. Sheet metal works doesn’t exist at all at the most part of the objects or is totally damaged on the part where it still exists.

The walls are damaged by capillary moisture.

Existing carpentry is wooden - dysfunctional in the most of its part, damaged and rotten. Installations in the facility, in the present state, are not operational. Electrical installations are partially distributed Water supply and sewage installations have been corroded over time.

There is no protection pavement around the building, which additionally helps to develop moisture in the walls.

All dismantling, demolition, concreting and other works that could damage the existing construction should be carried out carefully to avoid damage to the structural elements of the existing building.

Description of reconstruction and adaptation

The reconstruction and adaptation of the building provides a complete insulation of the building from the capillary moisture. This insulation is predicted by classical cutting of walls at the height of the lower elevation of the floor - with bitumen, as a permanent solution.

Complete insulation of the walls of the building from the outside and on the inside in accordance with the EE rules. Partial replacement of the roof structure is designed. Replacement of the roof structure should be carried out after dismantling of the roof covering and laths, and after seeing the degree of wear. The roof structure is partially replaced with a new made of fir timber of the 2nd class, dry and without falling nodes. The calculation of the roof construction will be elaborated in the part of the construction project. With the corresponding roof levels, remove the roof cover and laths and then replace the worn parts of the roof structure and strengthen the connections with angles and flat bars. Replace the entire roof covering with a new plain roofing tile.

Demolish mud filling and place the projected insulation layers in place between the roof beam. During the inspection of the inter-floor structure, replace all worn roof beams.

The project completed the replacement of a complete sheet metal works with a new sheet metal works made of galvanized sheet metal d = 0,55mm

Access concrete paths are projected around the building  with a buffer layer of grain with a tamping of up to 20 MPa. Cover the foundation walls and the object's plinth with a drainage foil designed for this purpose.

At the same time, complete reconstruction of electrical installations as well as the construction of a new water supply and sewage installation is planned. Rehabilitation of the existing floors that are made of earthen material, shall primarily be done by removing the soil layer at a depth of 20 cm. After that, concreting is to be carried out with a thin concrete 1: 4. After concreting follows the laying of layers of hydro and thermal insulation and applying a layer of lightly reinforced cement screed of 4,0cm. Place the projected floor coverings of granite ceramics on the cement screed

The project provides the construction of a suspended ceiling from fireproof gypsum card boards 3x 15mm.

The project the production of moping pergolas from 12x12 wooden beams, 38x40 cm piles and 380 cm high pillars. The purpose of the pergola is to protect bicycles from atmospheric disturbances and to temporarily gather cyclists.

Roof cornice-eaves of the building is to be done with planceer piece  of styrofoam and with  minimal profiling and treated with facade paint.. The order of execution of the works on the adaptation is as follows: demolishing of roof coverings and roof laths. Replacement of the worn out roof structure and its fixing. Removing the existing carpentry. Demolishing of wooden roof beams filling. Inspection and replacement of worn-out roof beams. Concreting of the ring beams of lintels.. Carrying out the removal of moisture from walls with the classic method of inserting waterproofing tape. At the same time, perform works on the installation of new plumbing and sewage pipes in accordance with the executive design that will be subsequently performed. Roof decoration and installation of vapor-permeable, waterproof foil over the boards. Nailing of 3x5 cm ventilating leafs. Over the roof laths , nail the laths to the plain roofing tile according to the manufacturer's instructions. Set the roof cover from the plain roofing tile. Perform the sheet metal works. Perform the waterproofing of the foundation walls and the footing with the tape for the drainage of the foundations. After these works approach to works in the interior of the building and at the end concreting access paths.

Construction of the building

The building is designed, ie reconstructed, with solid constructive brick walls of 30.0 and 50 cm thick. Composition of bulky - exterior walls is: mortar on the inside of the thickness of 2.5 cm, existing POSTO brick thickness 50.0 cm, styrofoam 8.0 cm, total thickness 60 cm.

Inter-floor structure above the ground floor is made of existing wooden beams with plank 2" nailed to the beams and with a layer of stone wool thickness 8 cm with hydro insulation layers and with finishing covering of gypsum cardboard.

Horizontal reinforced concrete ring beams do not exist, but will be provided by this project for the purpose of stiffening in the horizontal direction. These ring beams are carried out by cutting into the extensive walls up to a depth of 20 cm with the main reinforcement and the stirrups according to the bill of quantities that will be included in the construction design .The floor elevation of the ground floor is +0.20 m. It is retained as a elevation of a new concrete slab through which layers of hydro and thermal insulation will be laid.

The foundations of the building are the existing striped, made of brick, without protruding reinforced concrete ring beams at the height of the upper elevation of the floor. This foundation is checked by digging out, and if the condition is critical then execute the subsequent production of horizontal reinforced concrete ring beam. Perform the drainage around the object in order to allow the eventual atmospheric water to be discharged more easily outside the object. Protected reinforced concrete sidewalks are provided around the object. Connection of the object and with designed sidewalk shall be carried out with permanently elastic mass or bitumen.

Roof construction is a double slope roof type of wooden structures - purlin and rafter roof that also relay on wall plate designed walls. Roof creasing is from 0.00 to 30.0 cm.

The gutters are designed as hanging gutters from galvanized sheet metal.

Clear height of the ground floor is 300 cm.

Joinery in the building is of a hard wood painted with protective coatings based on wax.

All slopes of the roof are designed with a roof boarding (osb slab) and a double row of laths. Roof cover is a plain roofing tile.

External and internal   floors and walls finishes

The walls are painted from the inside, and on the outside they are treated with dispersion paints in the colours of the existing part of the building. Decorative plastic on the façade is made of styrofoam with a thickness of 3.0cm.The floors in the building are made of ceramic tiles and laminates depending on the purpose of the premises. The joinery in the building is made of solid wood, painted with protective coatings based on wax. Connection of façade joinery with a wall is carried out by fold from a styrofoam thickness of 3.0cm to avoid thermal bridges. Glazing is done with thermopan glass. Roof cornice-eaves of the building is to be done with pieces of styrofoam and with  minimal profiling and treated with facade paint. The plinth is made of concrete and plastered.

Conditions for the protection of adjacent objects

There are no objects  near the said object

Installations in the object

Installation of three-phase current as well as water and sewage installations is provided in the facility. Heating in the facility is provided by  electrical installation

2. DESCRIPTION OF THE SYSTEM FOR AUTOMATIC DETECTION AND REPORT OF FIRE

The basic elements of the system are: central device, automatic detectors, manual fire detector, alarm sirens and installation cables. The system is of conventional type. The central device (fire control panel) is located in the conference hall, all according to the graphic attachment. The central device is a conventional multi-zone switchboard to which the signal lines of automatic and manual fire detectors are connected. The display of the automatic fire signalling zone is given in the Graphics Documentation.

Laying of cable systems of automatic fire signalling is provided with HFKS pipes without halogen elements. In case of a possible passage of these cables through earth, cables must be  put in a protective OKITEN pipe.

Power supply of the central unit with electricity is provided from the main distribution cabinet in the building. The central unit has accumulator batteries with an electronic circuit for continuous powering of the entire system for automatic fire signalling in the period of 72 hours in normal operational mode  and 30 minutes in the alarm mode.

The fire control system provides the following functions and outputs:

- reception and registration of the signal of the occurrence of fire,

- protocol of all changes in the operation of the fire alarm installation,

- signalling of failure on primary lines,

- Signal of failure on the power source,

- signalling the connection with the earth,

- exits for alarm sirens and

- relay outputs for the executive functions of the control panel.

Alarm sirens are positioned so that the alarm signal is heard in all parts of subject object. The sirens are mounted on a wall or ceiling at a height of 2.5m from the floor. Horns with a flashlight are provided.

Choice of fire detector type

In the event of fire, smoke, temperature rise, and characteristic infrared and ultraviolet radiation occur. Depending on which of these side effects are expressed, a certain type of detector is selected, taking into account possible impairing factors that may cause a false alarm.

The purpose of the object is Hostel, with allowed smoking, so that smoke and other factors are likely to occur and  cause false information if smoke detectors are used. On this basis, conventional thermal smoke detectors shall be  in the boiler room where an optical detector is installed. In the rooms  where aerosol and smoke is possible, such as laundry, kitchen, etc. thermal detectors are provided.

On the entrances to the building and pedestrian paths, automatic hand-held detectors are provided so the system would be activated immediately after determining if  there is a real risk of fire spreading.

Alarm siren is foreseen to be located on the ground floor, and the other one on the first floor. Sirens are used to inform people about a fire hazard, and in places where there is a possibility of increase noise, it is possible to put flashlights with an alarm siren, which is done.

Executive functions of the fire fighting central device

In the event of a fire, by any automatic or manual alarm in the facility, central device through relay outputs can provide:

- turn on alarm siren,

- switch off power supply with electricity (depending on the technical and technological process in the facility)

- sending a recorded alarm message to 10 programmed phone numbers using an alarm telephone that is intended for assembly near the switchboard.

Forwarding the above-mentioned executing command  of systems for the automatic fire alarm s

is provided by using non-combustible cables NHXHX FE180 2x1.5mm² .