# VOLUME 3

# TECHNICAL SPECIFICATIONS

1. TECHNICAL DESCRIPTION  NEW AGRICO MARKET IN  BELA CRKVA - ARCHITECTURE

Object location

The object is built on a parcel no.  10447/62 KO B.Crkva, total area of 8070 m2.

The location includes the area between the streets 1st October , J.Popović and M.Tita Square.

The new market itself occupies the northern area of abovementioned parcel. With its construction line on the north longitudinal facade, it is set up along the southern street boundary of  M.Tita Square. The western façade - the building line of the object is moved in relation to the street boundary of J.Popovic Street for 10.00 m. to the East, which determines its position on the ground.

To the south of the object, there is an existing, partly reconstructed asphalt road that is planned for car traffic and is processed within this project.

Traffic solution

The project foresees that the main pedestrian access roadway will be from Street 1 st October. With the entrance to the building, there are areas for bicycle parking lot.

For the parking of motor vehicles, existing parking lots on the southern edge of the plot are used.

Pedestrians enter the building through mild sloped and covered ramps.

The access to light goods vehicles of the sellers of market goods as well as the parking space for them are projected from the south side of the building along the existing roadway. The supply of goods is provided through two entrances with a mild sloped ramp, through communication breakouts to the sales area. It is anticipated that the sellers of agricultural products with their smaller transport vehicles, come from the direction of October 1, pass the traffic lane of the southern periphery of the road, stop the vehicle and with carts, that will be provided for them in a special space, bring goods to their stalls, return the carts and remove the vehicle to the existing parking lots in the immediate environment of the market or out of parcel no.10447 /62.

Architectural solution

The object is the height P + 0 with the highest elevation point of the roof of 8.75m / 95.70

The ground level of the building is 86.95, but it can be adjusted and subsequently aligned with the levels of future projects of the surrounding roads and before marking the facility, without changing the scope of founding. The founding level is determined on the basis of data from the previously prepared geo-mechanical study.

Total net area of the building is 1,818.37 m2.

It consists of four connected units, pavilions A, B, C and tracts of covered and closed market.

A pavilion A has 6 commercial premises for sale of market goods: seeds, healthy food, garden tools and accessories, flowers, bread and pastry, etc. Each of the foreseen premise  has its own toilet lobby, toilet and some additional storage for goods . Access to the premises is in a small part from communication od market object, and mostly from the direction of the street 1st  October 1, so that they can function even at the time when the market does not work.

There are two meat and fish shops in Pavilion B, as well as special areas for milk and meat market. The total number of refrigerated showcases is 18. Each sales area of the meat and milk market has its own dressing room, anteroom and toilet and a place for the cooling chamber.

Pavilion C is provided for the area of market administration with offices, wardrobe for employees, sanitary facilities and a laboratory. In a separate room with access from two-way communication, a toilet is provided for users of market services and disabled persons.

With the approach from the direction of the road there is a tool store and a garbage area.

The largest part of the building is occupied by the projected area of the covered market with the planned 60 market stalls dim.100 / 140 cm. In the continuation of this part of the market, a closed part of the market with 54 stalls and 6 flower stalls is designed. The total number of stalls is 120. All spaces are connected with the covered communication. Beyond economic entries  and ramps, there is canopy of Lexan on a steel substructure

Between the area of heated market and pavilion B, the projected space is intended for technical needs. It is planned to enter the market as well as a part of the open-covered market, be fenced with a fixed fence in the line A columns and with lightly movable transparent perforated alum. in the direction of the E-E columns, which serve as a protection against the sun.

Construction of the building

The building is designed in the basic constructive modular network of 500x500 cm, which allows the application of several types of constructions either of concrete casting on the spot or semi-prefabricated and prefabricated construction. A combined system is chosen both for t the construction system and the choice of material.

Pad foundations are connected to reinforced ground beams or strips. Underneath the foundation and in the foundation pit, tampons from the compacted gravel d = 20 cm and a thin layer of plain concrete "layer of purity" 10 cm thick are made. Part of the footings and ground beams are located on the part which is now asphalted and it is necessary to cut and remove the asphalt.

For the part of the object above the ground, a skeleton construction of pillars of box-shaped HO profiles is provided, which are mounted on previously prepared base slabs anchored into the foundation beams or strips. Steel posts and grids are supported on the columns. The walled fills of brick blocks have a PP role and a task to seismically stiff the facility. The binding beams above the communication are ferro-concrete type Fert with reinforced concrete beams or horizontal ring beams..

Roof construction and covering

The roof structure above the open and closed market area is designed in a combination of steel purlins and trusses of a range of 15 m, stiffed by wind bracing. The roof structure above all the pavilions is designed from the same materials type frame, range 5,00 + 5,00 m. All non-inbuilt and non-walled steel parts of the construction are protected by anti-corrosive coating, PP coatings in accordance with PPZ elaborates and painted.

Roof cover is in accordance with the EE study, above the covered / heated part of the market, designed with the upper roof panel d = 10cm from double colored steel sheet metal and mineral wool filling, supported by the blinding purlin. The lower, suspended ceiling below the bottom of the lower truss  belt is the package d = 18 cm of ceiling gypsum plates with mineral wool layer 16 cm, all suspended on a grid made of galvanized profiles on a 60 cm distance.

Part of the non-heated area of the market-roof canopy is covered with insulating panels with 10 cm thick panel filling with mineral filler fillings, in order to reduce the possibility of forming hot air tampons under the roof covering in the summer period.

The porch, north-oriented and above  communication, is covered by a single roof TR sheet metal..

Above the non-heated area - straight AB plates, in order to prevent the condensation on  ceiling, a 10 cm thick insulation is installed.

Facade cladding

The larger part of the facade is made of facade insulation panels. The panel is made of double colored steel sheet metal with a mineral wool fill, a thickness of 12 cm in min.three colours, fixed, where indicated, for a substructure of 3 cm wide, total  thickness of package 15 cm.

Part of the facade cladding that forms the façade frieze on line A-A and above the level + 3.30m is made of painted insulating panels d = 6 cm of the same  quality and filled materials.

Parting walls made of brick blocks d = 20cm, between the non-heated and heated floor space (technological space, storage and waste) are covered in an unheated area with additional thermal insulation d = 8cm and protect with the lining of the light facade TR sheet metal TR 14/225 .

Parts of the facade made of masonry bricks on line A-A are also covered with colored  light facade sheet metal TR 14/225, on a light steel substructure..

External and internal metalwork

All external metalwork and metalwork in the part of roof light are aluminum, designed for climatic conditions and wind effects according to the standards for Belu Crkva.

All alu profiles should be of high quality with an interrupted thermal bridge. The glass package should be insulated and meet the conditions defined by the calculation of construction physics in accordance with the energy efficiency study.

The internal metalwork in the part of the closed market-heated space is with profiles of the same material. The fences are made of boxed profiles with a filling of   painted Q mesh or crimped wire mesh.

On the south façade of the non-heated part of the market, in order to protect from the sun, slide fascia panels are made of strengthen  alu profiles with filling of perforated aluminum sheet metal with associated suspension mechanisms and guides in the floor, which can be moved when needed and at the time when the market is not working , completely close the room..

Bearing and partition walls d = 20 cm

The project envisages the construction of walls of brick blocks d = 20 cm of walls in the flexible mortar, based on ferro concrete foundation  strips, ground beams  or steel sheeting rail. At the height of +360 from the floor, reinforced concrete horizontal ring beams are performed and walls which have the task of dividing the spaces on lines 1,4,17, have a ferro concrete horizontal ring beam as a finish.

On the part where it is foreseen, the raking ferro concrete horizontal ring beams shall be performed. A part of these walls built between steel pillars plays a role in the longitudinal direction, to stiff the object.

Internal partition walls

The internal partition walls are made of brick d = 12 cm up to the height above the suspended  ceilings. In the height above the door and on the top of the walls, it is mandatory to carry out ferro concrete horizontal ring beams connected with the external walls or pillars. The walls in the part of the market administration are made of gypsum lining on sheet metal galvanized profiles.

In the sanitary areas - public toilets, a part of the partition walls of light alu profiles with partitions and door wings  with filling of painted aluminum sheet metal, all raised in relation to the floor by 15cm

.

Interior processing of walls

Part of the masonry walls are plastered with flexible mortar, skimmed and painted, and the part is covered with ceramic tiles up to a height of 2.00 m. The sections of the inner surfaces of the facade panels as well as the joints of the ferro concrete horizontal and vertical ring beams with a steel construction are covered with gypsum slabs on a galvanized substructure .

Flooring

In all areas of unheated - covered markets, communications, as well as storage rooms and technical areas, a fero concrete d = 15 cm is foreseen as a supporting and ending floor layer.

In the closed part of the market, fero concrete d = 10cm is foreseen. In  meat, dairy markets, commercial premises and laboratories  anti-slip, acid-resistant ceramics on reinforced cement screed is envisaged with  total thickness of the coating and the bearing layer of concrete d = 8 cm, cast over the hard floor thermal insulation protected with PE foil, thickness of thermal insulation 5cm.

Suspended ceilings

In the area of meat market and meat and fish retail outlets, a raster ceiling of mineral plates with antibacterial finishing type AMF Hygena or similar/equivalent. Dimensions of the panels are 600x1200 mm, thickness 15 mm. The panels are placed in a visible substructure (system C), the width of the sub construction is 24 mm, with flat edges of the panels with clipped hangers for the roof construction. The ceiling panels  are factory-painted with antibacterial color that prevents the development of bacteria and fungi over the surface of the ceiling. In other shops and in the area of the market administration, there is a suspended  ceiling from plasterboards in which the lighting is located. The ceiling is placed under insulation from a layer of mineral wool 16 cm. In sanitary premises, a monolithic, waterproof gypsum cardboard with thermal insulation is 16cm.

Installations

In the facility will be installation for  water, PP networks, sewer, heating, ventilation-air condition, electric lighting, lightning rod, fire alarm, PA system, video and telephone.

Water and sewage installations

The facility will have sewage installations with connection to two-side street collectors. The deployment of sewage from the premises, drainage and the associated part of the east wing of the market will be connected to the shaft in the street October 1 determined by the conditions of the PE

"Vodovod i kanalizacija (Water and sewage)", is street collector of mixed sewage Fi 160cm parallel and away from the construction of the street 1 October 10.00 m.

The second part of the building - the west wing, on the future nearest sewerage in the street J.Popovića, which for now from the streets of Cvijiceva to Masarikova has no sewerage but is under construction. In the part where the projected horizontal water diversion and sewerage inside the building's overall structure passes through the construction foundation, it is foreseen to leave steel cuffs that will allow the passage of installations, without jeopardizing the stability and firmness of the foundations.

Due to the evident lack of data from the cadastre of underground installations - especially the external installations of water and sewage (the bottom of the channel in the shafts, the exact geodetic position of the installations with all the data and altitudes, etc.), all connections to the outer water and sewage system are projected to the control lines of the plot with connection or water meters in future green areas, closest to the site of existing street current and future collectors.

The connection of the western outlet of the installation of a new facility to the present and future street installations in the streets of J.Pović and Trg M.Tita will be the subject of designing and in the jurisdiction of the local PE "Vodovod i kanalizacija".

The internal sewerage in the part where meat and dairy products are sold will have specially built grease separators. The project envisages that the outlets in part A of the building have their own control water meters for measuring the consumption of water stored in their sanitary space or where the designer WS considers it appropriate the rest of the object and the internal PP Hydrant network, will have its own measurement.

On the southern edge of the future building, next to the sidewalk, there is an open shallow flume of prefabricated concrete elements 40x40 cm with several gulley for receiving water from the roofs and sidewalks of the building that will be connected to the new designed atmospheric sewage with connection to the shaft 2 in the street 1 October.

A more detailed technical description is given in a separate project of these installations

Installation of a high current

With the project of high current installation, it is envisaged to carry out interior lighting of the type of LED as well as the external lighting placed on the facade of the building. All commercial premises of have a sufficient number of equipment and appliance ports. It is planned to measure the el. energy for the entire object (according to the conditions of the distributor ) and all individual commercial premises(x 8) will have their own control measurements of consumption.

The electrical installation project envisages the implementation of protective grounding and lightning protection.

Installations for heating and cooling

Installation of heating installations, ventilation and cooling installations, as well as installation of heat pumps are foreseen. Above of a flat roof, the installation of the air-conditioning chamber is foreseen. When installing it, it is necessary to check their weight / suspension and, if necessary, to pre-design the ceiling plate. In the closed part of milk and meat market, cooling chambers and  showcases are planned.

A more detailed technical description is given in a separate project of these installations.

Landscaping

Around the building is a projected sidewalk tiled with already used and undamaged 40x40  exposed aggregate concrete slabs, with a concrete prefabricated curb and concrete  trench drain below each gutter.

Green areas are performed with concrete curbs, humus is filled, grassy lawns are planted with decorative shrubs of the species juniperus horizontalis or similar. Where it does not interfere with underground installations, planting of trees according to the choice of PE " Komunalac " is foreseen

2. TECHNICAL DESCRIPTION OF HYDROTECHNICAL INSTALLATIONS

Water supply installations

The connection of the newly projected water supply installation for the east section is foreseen on the existing street water network of 160 mm diameter made of PVC material in the street Marsal Tito, in accordance with the conditions of the competent PUC. Connection for the object is carried out using the KVP (Home Water Connection) saddle for connection with the valve, in such a way that the KVP saddle with valve for PVC water pipe DN150 / 1 "will be installed at the connection point. The saddle with a diameter of 1 ", with a telescopic set and a street capping on the connection (DIN 4056, weight 14kg).

Water connection to the street water supply network is carried out with water pipes of quality PE100, NP10, diameter OD32mm (1 "). The quality of the pipes must correspond to EN12.201 and the standard JUS ISO 4427: 2001. The water connection is designed in such a way that it goes straight in the direction of the street water pipe, without any horizontal and vertical turning to the part to the water meter connection. The plumbing pipe is laid on a layer of sand of 10 cm and is filled with sand up to a height of 10 cm above the tube's head. At the part under the road, a full closing of the trench is foreseen. The Contractor shall perform these works entirely in accordance with the instructions of the responsible person from the competent PUC.

For the measurement of water consumption, the installation of a central water meter measuring 3/4 "in diameter for measuring the consumption of sanitary water in the premises" east "is planned and it is located in the manhole " east "in front of the building, since at the given location there are conditions for the construction of a water meter manhole outside the building. In front of and behind the water meter, it is necessary to set the valves of the same diameter. The water meter manhole "east" is dimension 120 x 100 x 170 cm (light opening), which is projected from concrete block, wall thickness d = 20 cm on concrete slab of reinforced concrete MB25 d = 20 cm, and upper plate MB25 d = 20 cm. In the upper panel, a 600mm diameter cover for the load class C250 is provided.

All installations in the building are designed from PPR3 pipes of the appropriate diameter that need to be insulated with insulation type "Armaflex" or similar. These pipes must meet DIN 8077-8078 standards, as well as DIN 16962, as well as SRPS EN ISO 15874. In each commercial premise, there is one 10L electric water heater for sanitary space, except in the L6, which has another instantaneous sink water heater.

The connection of the newly constructed water supply system for the west section is foreseen on the existing street water network of 160 mm diameter made of PVC material in the street Marshal Tito, in accordance with the conditions of the competent PUC. Connection is carried out using cast iron fittings in such a way that the T-piece DN150 / 100 / 150mm is fitted at the connection point, with the appropriate coupling material - MULTI JOINT clamps E-type, diameter DN150mm. Behind the T-piece, the FF piece DN100 / 600 which enters  into the water meter manhole"west" is inserted. Water connection to the street water supply network is carried out with water pipes of quality PE100, NP10, diameter 110mm. The quality of the pipes must correspond to EN12.201 and the standard JUS ISO 4427: 2001.

The water connection is designed in such a way that it goes straight in the direction of the street water pipe without any horizontal and vertical turning to the part of the water meter in the water shaft. The connection water pipe is laid on a 10 cm sand layer and filled with sand up to a height of 10 cm above the tube's head. At the work under the road, a full closing of the pavement is foreseen. The Contractor shall perform these works entirely in accordance with the instructions of the responsible person from the competent PUC.

For the measurement of water consumption, it is foreseen the installation of main - central water meters, which is 1 "diameter for measuring the consumption of sanitary water in the business part" west ", as well as the water meter diameter DN80mm for measuring the consumption of water on the hydrant network, located in the water-meter manhole "west ", since there are conditions for construction of a water meter manhole outside the facility at the location in question. In front of and behind the water meter, it is necessary to install the valves of the same diameter, in everything according to the graphic detail. The water meter manhole "west" is dimension 200 x 140 x 170 cm (light opening), which is made of concrete block, wall thickness d = 20 cm, on concrete slab MB25 d = 20 cm, as well as upper plate MB25 d = 20 cm . In the upper panel, a 600mm diameter cover for the load class C250 is provided.

The diversion for the sanitary net goes from the water meter manhole "west" with water pipes PE 100 pipes of diameter OD 40mm, for working pressure of 10 bar. Place the pipes in the building with mandatory insulation type armaflex or similar.

As required by the conditions, part of the central administration has a separate water meter, as well as the commercial premises B.L1 and B.L2 (meat and fish) - a total of 3 pieces. The centrally operated water meter is ¾ ", and the water meters for commercial premises B.L1 and B.L2 are diameter ½" with the valve in front and behind the water meter of the same diameter, for measuring the water consumption in each commercial premise individually.

DHW installations for the needs of business units in the building are designed from PPR3 pipes of the appropriate diameter that need to be insulated with "Armaflex" type or similar type. The distribution of plumbing installations in residential units is also of the appropriate diameter of the PPR3 material. These pipes must meet the SRPS EN ISO 15874 standards. In all business units, the sink is designed for flow electric water heaters with a capacity of 10 liters.

Sanitary water distribution network.

The basis for the east section is the PE pipe Ø 32mm NP10 with branches to the premises in the building. It is tied to the watermeter manhole "east" in the yard of the complex. A total of 1 sanitary water intake has been designed into the building for the east part. This water line enters the building. It ends with a valve of diameter 1 "in the building, from where it starts distribution to the commercial premises.

The basis for the "west" part is the PE pipe Ø 40mm NP10 with branches to the premises in the building. It is tied to the watermeter manhole "West" in the yard of the complex. A total of 1 sanitary water intake has been designed into the "west" part. This water line enters the building. It ends with a valve of 5/4 "diameter in the building, from where it starts distribution to the commercial premises.

Water supply network - external and internal hydrant networks..

The outer hydrant network is designed as a ring net, pipes PE100 Ø 110 NP10 SDR17 in all according to SRPS EN12201 + 2: 2008, which is connected to the street water supply network via a water meter in a water meter manhole and on which the above-ground hydrants are installed (according to the situation plan delivered by the Investor ) and pipes PE100 Ø 75 NP10 SDR 17 as inputs of the internal hydrant network into the building. The power supply is from a street water network with a pressure of about 4 bar.

The required amount of fire extinguishing water by the external and internal hydrant network is 10.0 l / s.

As already mentioned, a diversion for an external hydrant network is provided with PEHD pipes of 110mm diameter, for a working pressure of 10 bar, which goes through the yard of the building. The pipes are placed at a depth of 1.30-1.40m. They are placed in a layer of sand 10 cm below the tube and 10 cm above the tube. It is planned to install a total of 4 (four) external fire overhead hydrants of diameter DN80, GGG H = 1850mm, in all according to SRPS EN 14384.

The distance between the two external hydrants is less than or equal to 80 m, which is in accordance with Article 17 of the Rules on technical norms for the hydrant fire extinguishing network ("Official Gazette of SFRY", No. 30/91). The external hydrant hoses are positioned in such a way that they are protected against mechanical damage and freezing.

External overhead hydrants are placed on the complex of the market so as not to impede traffic and foreseen activities. Hydrants are positioned so that they are always accessible and are indicated by tables with entered distance from the mark to the place where the hydrant is located.

In addition to each hydrant, a metal cabinet with extinguishing equipment for the overhead hydrant is installed. (The dimensions of the cabinets are 1080 x 540 x 185 mm, with 4 trevira hoses f diameter of 2" 15 m, 2 nozzles diameter 2" with a 16 mm diameter outlet, 1 overhead hydrant key and 1 key ABC and C). All hydrant cabinets must be visibly marked with a hydrant mark (letter "H").

In front of each hydrant, it is necessary to set EURO 20 DN80 closures with telescopic set and capping for valve.

An internal hydrant network is foreseen in the facility. The required amount of fire extinguishing water by the internal hydrant network is 5.0 l / s. The internal hydrant net flows from the yard to the vertical of the inner hydrant network with PE100 pipes with a diameter of 75 mm.

Distribution through facility is provided on the walls of the building with galvanized water pipes 65mm (2 1/2 ") and 50mm (2") pipes, at a height of 3.5m from the floor of the finished floor on steel carriers with rubber pads at every 2.0m. These installations must be insulated with "Armaflex" type insulation in standard SRPS EN 13501-1 (flame-retardant) or similar. In the whole facility it is planned to place a total of 5 internal wall hydrants of diameter 52 mm in all according to SRPS EN 671-2, at 1.5 m from the floor of the floor.

It should be noted that it is necessary to perform additional isolation on the line of the hydrant network in conditionally unfinished premises in agreement with the designer and the supervisory authority.

Prior to commissioning of the water supply network, the pipeline should be tested. Perform the test procedure by closing the entire network and pit it under the pressure which is 1,5 times bigger than the operating pressure, and not less than 9 bar. The network that is loaded and closed in such a manner is kept under the pressure for 24 hours, so if you do not notice the drop in pressure, the network is correct and can be put into operation. After the test has been carried out and the correctness of the network has been completed, the minutes signed by the investor, the contractor and the supervisory body shall be prepared.

After the control has been carried out, it is necessary to make a report on the performed control indicating the measured values, as well as the date and time of the measurement.

The hoses located in the hydrant cabinets are controlled at least once a year, and are tested at a water pressure of 7 bar. Hoses that indicate leaks during testing should be replaced with correct ones.

Route of the water line

The projected water supply network is mainly from the newly designed roads of the existing complex in green areas. Sporadically, and where it is not possible to apply another solution,  as a passage through existing and newly designed pavement structures.

The route of the pipeline is defined by the project task, the position of other installations, overhead and underground, and direct agreement with the Investor.

Pipeline finished grade

Pipeline finished grade is designed with a minimum installation depth of 1.30m - 1.40m (bottom of the pipe) and is installed mainly to monitor the existing levelling of the roads, whereby it is necessary to take into account crossing with other infrastructure facilities.

Trench

The projected width of the trench is conditioned by the diameter of the pipe, the depth of the trench and the method of installation. The projected width of the trench is 0.60 m.

Pipes lay on a layer of sand 10-20 cm thick. The pipes are coated and sanded and covered with sand 10 cm above the hub.

The backfilling of the trenches on the part of the route of the water supply line carried out in the green belt is done by the excavated soil, with the backfilling in the layers of 30 cm and compacting to the natural load of the soil, and on the part of the route that passes through the pavement construction, the complete replacement of the material by the gravel of natural granulation is performed; the technology that is foreseen in the project of roads on the complex..

Pipe material

Designed distribution water network through the yard of the complex is of diameter 110mm, 75mm and 40mm high density polyethylene PE100 for nominal pressure of 10 bar. The connection of the pipe is done by welding. The drainage of plumbing installations is carried out by polyethylene arches that connect with pipes to each other by welding.

The arches are anchored in the base material. Anker blocks made of concrete MB20 are not required. The selection of the pipe material was done taking into account the quality analysis and the present conditions on the market.

Installations of foul sewer

Installation in and outside of the facility is solved in the most appropriate way, and dimensioning of the pipes is done according to the general system.

In the mentioned area, there is a street sewerage network of the general system in street 1. Oktobra, and there is no street sewer network in Jovana Popovića Street, but a new sewerage network, that is not the subject of this project, will be launched. There are two sewage connections from the facility. For the eastern part of the building, the connection is planned on the existing sewage collector in the street 1. Oktobra, the sewage PVC pipes 160 mm in diameter, in the fall of 2%, through the inspection manhole in which the wastewater from the building is poured, with a revision in the mentioned manholes, diameter 1.0 m, which are located inside the building (RŠ4, RŠ5) and outside the building (RŠ6), where RŠ6 is located at about 4.5m from the control line in the green area. (RŠ=Inspection Manhole)

For the western part of the building, the connection is foreseen for the future sewage collector in Jovana Popović Street, PVC pipes with a diameter of 160mm in fall of 2%, through the inspection manholes in which the wastewater from the building is poured, with a revision in the mentioned manholes, diameter 1.0 m , which are located inside the building (RŠ1, RŠ2) and outside the building (RŠ3), where RŠ3 is located about 1.5m from the control line in the green surface. This line also accepts wastewater from the premises where milk and meat products are sold. This line includes a grease separator. A 2.0 l / s grease separator is selected here, from polypropylene for installation in a green surface, according to EN 1825-1. The outlet pipe after the separator of the grease is 160 mm in diameter. The connection of the grease separator and the incoming and outgoing pipes should be carried out by flexible couplings. Install the separator in accordance with the manufacturer's instructions. On the line of greased wastewater inspection manholes RŠ7 and RŠ8 are provided.

The distribution of the foul sewer  inside the building goes below the floor slab of the building, provided the pipes pass under the base strips and underlying beams, the sewer pipes of diameter 50mm, 110mm and 160mm with inspection manholes. The quality of the pipe must be SDR41, the strength of the ring is SN4 kN / m2. It is possible to install another type of pipe, but with mandatory consultation with the designer. The sewage pipe is laid on a 10 cm sand layer and filled with sand up to a height of 10 cm above the tube's head. These works shall be performed by the contractor in full compliance with the instructions of the responsible supervisor. The minimum installation depth is 0.80 m. Falls on the sewerage network are projected in the slope of 1.0-1.5% towards the connection manhole. It is noted that a protective steel tube of 250mm diameter, L = 600mm is projected under each foundation strip or foundation beam, and the intermediate space must be filled with permanently elastic material.

Waste water from the plateau of the common part of the market and in the area of the meat and milk shops is collected through a polymer concrete channel V100 type with galvanized gantry drainage grate with vertical drain DN100 for the load class B125 in accordance with SRPS EN 1433. The channels with drain grids are to be carried out in according to the manufacturer's instructions.

Also, in the premises for meat and milk, it is planned to collect condensate from refrigerating showcases with sewage pipes 50 mm in diameter, and the cooling box connection itself is provided through a condensate siphon 40/32 mm. The siphon must be equipped with a mechanical and water block and a cleaning pad. The siphon seal connection with sewage pipes is carried out using a short sleeve with rubber sealing ring DN50 / 40 mm

The distribution of the foul sewer outside the facility is provided below the future road and green areas, with sewer pipes of 160mm diameter and 200mm with inspection manholes. Connection to the inspection manhole is carried out using PVC sewer pipes with a diameter of 160 mm. The quality of the pipe must be SDR41, the strength of the ring is SN4 kN / m2. It is possible to install another type of pipe, but with mandatory consultation with the designer. The sewage pipe is laid on a 10 cm sand layer and filled with sand up to a height of 10 cm above the tube's head. These works shall be performed by the contractor in full compliance with the instructions of the responsible supervisor. The minimum installation depth is 0.80 m. Falls on the sewage network are projected in the slope of 1.5% towards the connection shafts.

Inspection manholes are the design of reinforced concrete rings with lengths of 1.0 m and 0.5 m, a taper end piece length of 0.60 m and a mounting bottom part with the channel pipe. A total of 8 inspection manholes have been designed on the line of foul sewage.

The lower mounting part is placed on a prepared gravel substrate d = 10cm, floor slabs of concrete MB20 d = 20cm and reinforced concrete floor slabs d = 15cm. After that, mounting of the joints are interconnected by waterproof cement adhesives.

The inspection manhole ends with a conical part on which the cast iron cover is laid. The cover should be screwed with a concrete ring in everything according to the graphic detail. From the inside, to be waterproof, inspection manholes are coated with penetrate in three layers.

Sewage verticals are 110mm diameter. Twelve verticals for foul sewers are projected. The sewerage verticals and the lower sewer distribution in the building are made of plastic PVC pipes of appropriate diameters. Above the floor, inspection eyes are placed on the verticals for possible interventions on the network. They are covered with nickel-colored openings for maintenance.

On verticals and horizontals, it is mandatory to install inspection eyes and inspection manholes. At the end of the vertical there is a ventilation cap made of galvanized sheet metal.

Complete backfilling of the pipeline should be performed after testing the waterproofing of the joints, in the layers of 20 cm with manual pouring, taking care that the pipe does not damage..

Atmospheric water sewage installations

For the project facility, collecting and draining rainwater from the roof and the road around the building is planned.

For the acceptance of atmospheric  water from the roof, the architectural project envisages 21 gully verticals OV1-OV21. Atmospheric water from the roof of the building is freely discharged into the green surface through the gantry verticals OV1-OV8, OV14-OV19, from the gutter verticals that enter the object OV9, OV10, OV13, OV20 is drawn out with PVC pipes with a diameter of 160mm p = 1.5% into newly designed manholes  of atmospheric sewage, and from the gantry verticals OV11, OV12, OV21 and from the new projected roadway - the plateau is taken to the newly designed concrete drain flume with concrete "drum" gullies with gratings 400 x 400mm (total 6 pieces BS1-BS6) and is carried away by inspection manholes to  the street network of the general sewage which is located in street 1st October. Gray concrete flumes with a dimension of 40x40x12cm are projected, on the substrate of concrete MB20, thickness d = 10cm, in the total length of 102m. Inspection manhole is carried out using the same technology as for the foul sewage  network. Inspection manhole  on the line of atmospheric sewage are marked from ARŠ1 to ARŠ7.

The distribution  of the atmospheric sewage outside the object of the facility is provided below the future road and green areas, with sewage pipes of 250mm diameter with Inspection manholes. Connection to the inspection manhole is made using PVC sewer pipes of 250mm diameter. The quality of the pipe must be SDR41, the strength of the ring is SN4 kN / m2. It is possible to install another type of pipe, but with mandatory consultation with the designer. The sewage pipe is laid on a 10 cm sand layer and filled with sand up to a height of 10 cm above the tube's head. These works shall be performed by the contractor in full compliance with the instructions of the responsible supervisor. The minimum installation depth is 0.80 m. Falls on the sewerage network are projected in the slope of 0.5% towards the connection manholes.

Sanitary appliances

All sanitary fittings foreseen by the project are of the first class and must be equipped with the appropriate fittings for normal operation. It is noted that in the toilet intended for the disabled person, there is also provided adequate sanitary equipment specified by the bill of quantities. It is also necessary to examine all sanitary fittings before its use and correct all damages.

The following heights are projected from the floor for sanitary water connections

:• WC, trocadero  0.70m

• Wash basin 0.50m

• Sink 0.50m

• Hot-water heater 0.50m

3. TECHNICAL DESCRIPTION ELECTRICAL POWER

Connection:

The low voltage connection will be processed from the existing TS "DOM ZDRAVLJA" in accordance with the applicable distributor conditions. The low voltage connection is not the subject of this project..

Distribution cabinets

The main distribution cabinets of the facility are located in a separate room (technical room). GRO-1 and RO-TP. GRO-1 are located in this area. The GPRO-1 is supplied from the cable connection cabinet KPK-1, and this from the special extract from the power substation. Near the substation the KPKEV-2P and POMM6 are installed with the measuring group all in accordance with the terms and conditions of the distributor. The scope of this project ends with KPK-1. In GRO-1 are located control electricity measurement units for all commercial facilities. It is possible to connect GRO-1 to an external mobile unit. This aggregate is not the subject of this project. The RO-TP covers the users of the business facilities and the area of the covered market. The consumers of the mechanical installations will be supplied from RO-TP. The RO-A is located in a technical room near the air conditioner chamber. The RO-KA is located above the roof near the compressor aggregate.

Installation

It is implemented with N2XH type conductors (Non halogen cables with reduced emission of fumes, reduced flame propagation and flame isolation function). Installation is of a type for the wall and partly in the wall in the commercial premises. The cables are driven by newly installed metal mesh cable carriers, metal racks or with suitable clamps. In places where electric cables are sold through the boundaries of the fire sector, a protective coating and a certain fire resistance is installed. From the distribution panels to the refrigerating showcases it is necessary to place hard PVC pipes partly in the floor to each of the showcases. All installations are in protection min IP54, except in business part and in some commercial facilities where the IP20 is.

Lighting

The illumination of the subject space is with new LED lights. Lighting is in protection min IP54. The object's exterior is lightened by reflectors mounted on the facade of the building. The control of the illumination of the closed, market, open market, communication and the outer space is the cam switches from RO-TP (technical room)

Installation of anti-panic lighting

It is carried out on a special circuit with the help of luminaries with a local power source in the ready connection. The lamps are automatically switched on with the mains voltage disappearance, and are positioned to provide the necessary illumination on the evacuation corridor. They are scheduled for three-hour continuous operation.

Lightning rod installation

Introduction

This project dealt with a technical solution for atmospheric discharge protection for the subject facility. The second level of protection was obtained by calculating the efficiency of the lightning protection installation according to SRPS IEC 1024-1-1.

The object according to the classification belongs to the usual objects and the consequences of lightning strikes in this type of object are: loss of human lives (due to dangerous contact touch and step), fire, mechanical damage and damage to electrical installations.

In order to protect against consequences due to lightning strikes, we apply the appropriate protective measures defined by the standard SRPS IEC 1024 and the provisions of the new standard SRPS EN 62305.

Protective measures are: installation of lightning rod , equalization of potentials of metal masses (parts) on the building, properly dimensioned and installed grounding and application of overvoltage protection (in the project LV installations).

For the subject facility it is foreseen to install the receiving system and connect it to the down  conductors. The groundbreaker is ring-shaped with twenty-five earth wires for the ground conductors and earthworks for metallic masses (gutters, heat substations, DEA, ...) and the main equipotential of potentials.

Receiving system

A network of conductors is installed on the roof in accordance with the defined level of protection and prescribed protective measures. During the development of the solution, modern software for checking the protection zone (Shield) ; checking was done with  the rolling sphere corresponding to the required level of lightning rod installation.

The receiving system consists of a conductor wire net made of wire-aluminium (Al) Ø10mm (S = 78.5mm2). Aluminium is used as a material that provides efficient (less specific resistance), permanent protection (long lifetime), due to easier manipulation (lower mass), without anticorrosive protection and savings in the time required for assembly. The receiving system conductor is mounted on the thermo panel with the SON16 alike type.

Down conductors

It is provided to set the conductors on the typical distances. The down conductors are made of wire-aluminium (Al) Ø10mm and are attached to the wall by type ZON03 carriers. On each down hole conductor, the measuring point of the measuring joint with the separation element is foreseen (the cross piece of the strip-wire alike type KON02). It is foreseen that the vertical protection VZ is to be installed.

Grounding system

The earth electrode is placed in the foundation of the object. The designer has decided to use durable materials like stainless steel RH1 Rf 30v3,5mm l. For each measuring compound and the gutter vertical there is one earthling lead. The gutter verticals are connected with clamps to the ground.

In accordance with SRPS IEC 1024-1 and SRPS EN 62305, the earth electrode must meet the minimum prescribed length according to Figure 2 (for horizontal grounding l1 = l, for horizontal l1 = l / 2).

Checking the earth electrode according to the requirements of standard SRPS IEC 1024-1:

The earth electrode will satisfy the ground resistance less than 1250 Ωm. According to the composition of the land on which the object is located the given value is satisfactory.

Equipotential bonding

Equipotential bonding is carried out using a stainless steel strip of 30x3.5mm and a copper conductor min P 1x6 mm2 or aluminium 10mm2. By connecting all metal masses that are not under voltage in the normal operation, the equipotential bonding is achieved. All mechanical equipment, air ducts, metal cable carriers, hydraulic net and all other metal parts.

Protective grounding

The grounding is connected to the foundation earth electrode and is connected to the distribution cabinet through the bus bar of equipotential bonding.

Testing of the electrical installation is provided with issuing an attestation by an authorized company.

4. TECHNICAL DESCRIPTION FOR MECHANICAL INSTALLATIONS

Mechanical installations

Offices and shops are provided with heat pumps. Heat pumps with inverter compressors are foreseen, which operates in the heating mode up to -15 declaratively. In addition, each outdoor unit is provided with a heating cable of condensate plate  for the coding process so that the dissolution process is faster and more efficient..

The closed market is treated with an air conditioner. Attached there are two calculations for air conditioning chambers. The first calculation is for standard design conditions, the other is optimized.

According to standard conditions, about 45 kW of heating is required.

The Chamber has the following sections:

Mixed section, two filter sections, M5 and F9, electric heater, power 24kW, consisting of 6 power heaters of 4kW. and evaporators / direct expansion capacitors. The chamber is equipped with a automatics e that runs a heat pump. Automatic control must be of the same manufacturer as the heat pump..

Temperature and humidity sensors are located in the mixing section, after the electric heater and after the evaporator / condenser or on the output channel.

The blinds are analogue with feedback, in the event of a power failure, they are closed.

PLC for controlling the chamber has two spare digital inputs and one analog input. A signal from the fire control panel that stops the operation of the chamber, the operation of the heat pump and closes all the valves is brought  separately.

Filter replacement indicators can be separated

Cooling installations

A part of the facility is intended for the sale of food that require cooling. Within the market there are 4 commercial premises equipped with refrigerating showcases and one refrigerant chamber. Two commercial premises are provided with 10m of refrigerated showcases, the other two with 3m of refrigerated showcases. Disposition of premises and equipment within the facility is shown in the Graphic documentation.

Refrigerating showcases with a standard length of 1250mm are planned. All showcases are placed in the line. The showcases have their own evaporators with fans, and their own processors for controlling the operation of the showcase. The evaporators include built-in electric heaters designed for dissolution. The processors are housed in showcases and show the instantaneous air temperature in the showcase on the display.

The cooling chambers are designed with an air temperature from 0oC to 4oC. The projected daily intake is 500kg with an input temperature of 12K for 12 hours of cooling. The thickness of the thermal insulation panels in the walls and ceiling of the chamber is 8 cm, and in the floor 5 cm. Cooling / freezing and melting cycles in all chambers and showcases are alternating and switched automatically with the appropriate controllers.

All showcases and all chambers are connected to one central compressor unit. The compressor aggregate consists of three parallel compressors of different capacities, so seven-speed capacity regulation is enabled: 24% - 32.8% - 43.2% - 56.8% - 67.2% - 76% - 100%. Capacitors are adopted as air cooled, which provides relatively low operating costs.

On the aggregate there are electro-cabinet, protection and regulation equipment, manometers. Regulation of the compressor aggregate and condensate capacities are controlled via controllers and pressure probes. This regulation is completely automatic based on the measured values of the pressure on the suction and the thrust.

Evaporators and their fans are located inside the casing of the showcases and are delivered as an integral part of the showcase. The entire length of the showcase is provided with line drains, in which the drainage pipes from the showcase are supplied.

The evaporators in the chambers are ceiling type and have fans, i.e. provide for forced cooling. This ensures faster cooling of fresh goods entering the chambers. The drainage of condensate from the evaporator chamber is carried out into dotted drains, located in the toilets, located in the immediate vicinity.

The compressor aggregate and the condensate are intended to be located on the roof of the building.

All installations are designed with Freon R404A as a refrigerant fluid, for which there are no legal restrictions on the application

5. TECHNICAL DESCRIPTION FOR THE ROAD CONSTRUCTION

Vehicular roadway

On the south side of the building there is an existing paved parking lot that is not provided for reconstruction. Due to the newly constructed facility, the existing access to the parking lot from Jovan Popović Street is necessary to be expanded.

The project envisages the complete excavation and expansion of the existing roadway. The length of the axle of the extended roadway is 70.0m.

Finished road level is defined so as to ensure quality drainage of the traffic surfaces and adequate fit in the surrounding existing and planned facilities.

The alignment of the finished road level is min 0.50% and is oriented towards the existing parking lot and towards the street Jovan Popović.

Only the concave curvature Rv = 300m was applied from the vertical curvature.

The newly designed road is 5.0m wide and is bounded by concrete curbs 18/24. The tcross section slope of the road is one-sided, it is oriented to the left side and amounts to 2.0%.

Drainage of the road is done with the help of a drain flume that is placed along the left edge of the roadway.

The water from the drain flume is directed to the drainage tank, into a closed drainage system.

Elements of longitudinal and cross section profiles were adopted to provide quality drainage conditions.

The road structure consists of the following layers:

o Road surface  AB 11  4cm

o Bituminous support layer BNS 22  7cm

o Stone aggregate fraction 0 / 31.5 mm  15 cm

o Stone aggregate fraction 0/63 mm  25 cm

Pedestrian plateau

The project foresees that the main pedestrian access roadway will be from Street 1 st October. With the entrance to the building, there are areas for bicycle parking lot.

The pedestrian walkway was processed in the form of a plateau, whose surface is 375m2 ,together with a bicycle parking lot .Plateau is defined by Axis 2 whose length is 27.76m.

The plateau is defined in detail points, and at the characteristic points are shown cross sections.

The projected longitudinal and cross section slopes of the plateau provide undisturbed drainage. The plateau alongside the vehicular roadway is bounded by 18/24 concrete curb, which is erected vertically+ 12cm from roadway. Green surfaces are bounded with concrete curb12/18.

The construction of the pedestrian plateau consists of the following layers:

o Concrete slabs 5cm

o Sand 5cm

o Stone aggregate fraction 0 / 31.5 mm 20 cm