## Sheet1
Note: Tenderer should write numbers in yellow field and to delete name of currency in G4 and H4 which is not been used
VOLUME 4.3.2 — BILL OF QUANTITIES
Item | DESCRIPTION | Unit of measurement | Quantity | Jedinična cena (DM) | Kurs 1DM= | Price RSD/EUR | In total RSD/EUR
I PREPARATION WORKS-Dismantling and demolition
1 | Dismantling of existing roof cover with all layers and lowering it to the ground, all on the main facility part – sport rink; diassembled material is loaded and transported to rubbish dump 10km away. Calculation per m2 | m2 | 2200 | 10 |  |  | 0
2 | Dismantling of existing roof cover with all layers in the sports hall annex, the part which has AB ceiling; disassembled material is lowered to the ground, loaded and transported to rubbish dump 10km away. Calculation per m2 | m2 | 558 | 8 |  |  | 0
3 | Dismantling of existing roof cover with all layers at the part of annex which has a floor above the official entrance; diassembled material is lowered to the ground, loaded and transported to rubbish dump 10km away. Calculation per m2 | m2 | 45 |  |  |  | 0
4 | Dismantling of existing roof cover with holding steel INP profiles and placing all other layers to the ground; loading and transporting it to rubbish dump 10km away. Calculation per m2 | m2 | 87.5 |  |  |  | 0
5 | Dismantling of existing galvanised metal flashings which are in bad condition, lowering them to the gorund; calculation per 1m of removed material | m1 | 456 |  |  |  | 0
6 | Demolition the outer basement wall made of hollow clay blocks for the purpose of ventilation system repair. Construction waste is to be loaded into trucks and transported to rubbish dump 10km away. Calculation per m3 of pulled down wall. | m3 | 6.7 |  |  |  | 0
7 | Dismantling of existing channel glass with basic frames the position of which is in north-east facade. Removed glass and frames are delivered to the investor. Calculation per disassembled set. | set | 1 |  |  |  | 0
8 | Dismantling of reinforced glass and steel frames as well as lexan diffuser at skylight above annex. Calculation per set disassembly. | set | 1 |  |  |  | 0
9 | Demolition the outer basement AB wall with the purpose of ventilation equipment repair. Construction waste is to be loaded into trucks and transported to rubbish dump 10km away. Calculation per m3 of the pulled down wall. | m3 | 4.75 |  |  |  | 0
10 | Dismantling of metal door with frame positioned at the annex on north-east façade. Removed door is delivered to the Investor. Calculation per piece of removed door. | pcs | 1 |  |  |  | 0
11 | Dismantling of metal door and ventilation grid at ventilation channel on the north-east annex façade. Calculation per set of the executed work. | set | 1 |  |  |  | 0
12 | Dismantling of existing metal door at fire escape stairs. Calculation per piece of removed door. | pcs | 1 |  |  |  | 0
13 | Dismantling of all existing metal flashings, lowering them on the ground, the price includes use of scaffold. Calculation per set of executed position | set | 1 |  |  |  | 0
14 | Extending holes in AB channels for future gutter positioning on north-east façade. Calculation per set of executed position. | ser | 1 |  |  |  | 0
II EARTHWORKS general conditions
15 | Excavation of III category earth using machinery at the level of basement with the purpose of enabling unobstructed approach to mechanical equipment of ventilation which is to be repaired. Excavated earth is laid aside since it will be used later for covering the ditch. Calculation per m3. | m3 | 64 |  |  |  | 0
16 | Filling up the pit with excavated earth in layers 50cm thick with compaction. Calculation per m3 | m3 | 54 |  |  |  | 0
17 | Transport of remaining earth to town rubbish dump up to 5km away with loading and unloading using machinery and rough planning. Calculation per m3. | m3 | 10 |  |  |  | 0
III CONCRETE AND REINFORCED-CONCRETE WORK
18 | Purchase of material, use of mechanical equipment to make and lay concrete MB 30 reinforced concrete wall of basement which was pulled down for the purpose of repairing mechanical ventilation system; wall is d=25.00cm thick. Works are to be executed in accordance with the project, statics calculation, details and general description for concrete works. Concrete is laid and maintained in accordance with regulations. Price includes placing reinforcing bar, necessary planks, support and additional scaffold. Required plank is 6.66m2/m3. Calculation per m3. | m3 | 2.2 |  |  |  | 0
IV REINFORCEMENT WORKS
19 | To supply, transport, processing and installation of processed reinforcement for reinforced concrete basement wall d = 25.00 cm. | kg | 121 |  |  |  | 0
V MASONRY WORKS
20 | Procurement of materials, transport and wall bricking d = 25,00 cm in flexible plaster of ratio 1: 2: 6. Blocks shall be wetting before built-in. Place the first row of wall blocks in a layer of flexible plaster approx. 2cm thick. All openings are rejected. Calculation per m2 with the required scaffolding. | m2 | 1.4 |  |  |  | 0
21 | Supply of materials, transport and processing of devastated evacuation staircase and concrete fence Sika MonoTop-412N by one-component reparative plaster resistant to mechanical, chemical and fire effects that can be applied by machine or manualy without the prior protection of any visible reinforcement. The use of the scaffold is required. Calculation per m2 of damaged concrete surfaces. | m2 | 182 |  |  |  | 0
VI INSULATION WORKS
22 | Supply of material, transportation and production of waterproofing retaining walls (ab and brick) basement level (vertical surface) - PVC waterproofing system, SZT Position: AB wall of the building as a substrate of waterproofing. - PVC elastic waterproofing membrane Sika Plan 14.6 or equivalent, 2 mm thick, freely laid, welded with hot air at the ends, fixed (welded) on the Sika plasticized profiled mold or similar. and sealed with permanently elastic polyurethane material SikaFlex 11FC or equivalent. − geotextile 500g/m2 (felt) as a protective layer (overlap over 10 cm). Calculation per m2 of total surface without overlapping. | m2 | 5.35 |  |  |  | 0
23 | Procurement of materials, transport and production of waterproofing of the entrance staircase and plateau under the canopy with SIKAlastic 1K polymer coating or equivalent, which endures negative hydrostatic pressure. Insulation shall be done over a completely dry and clean concrete substrate. Layers are applied in two directions mutually in normal position, calculation per m2 of applied waterproofing mixture. | m2 | 165 |  |  |  | 0
VII SHEET-METAL WORKS
24 | Procurement of materials, transport and flashing of all roof surfaces with galvanized sheet metal of developed width (DW) 60cm, thickness 0.60mm. Apron flashing made of galvanized sheet metal are of different shapes. Flashing is carried out according to the details and instruction of the designer. Calculation per m1 of the developed area, all complete. | m1 | 538 |  |  |  | 0
25 | Procurement of materials, transport and installation of apron flashing around lantern of galvanized sheet metal, developed width (DW) 40cm, thickness 0.60mm. Galvanized steel sheets are of different shape. Flashing of lanterns in accordance with the details and instructions of the designer. Calculation by m1, all complete. | m1 | 115.2 |  |  |  | 0
26 | Procurement of materials, transport and installation of galvanized steel lined and hunging gutters, developed width (DW 28cm, thickness 0.60 mm. Connect the gutters with the rivets, in one row with a maximum space of 3 cm and solder with tin of at least 40%. The gutters should be made of galvanized flange 25x5 mm and threaded on the front of the gutterwith rivets of 0 4 mm, at spacing up to 80 cm. Calculation by m1, all complete | m1 | 356 |  |  |  | 0
27 | Procurement of materials, transport and installation of galvanized sheet metal flashing on the canopy above the entrance, all according to technical details, calculation according to m1 mounted flashings | m1 | 56.65 |  |  |  | 0
28 | Procurement of materials, transport and installation of canopies flashings with southwest façade, paneling of windows on demit facades, flashing of ventilation holes, windows on the northwest facade, around the door on the evacuation staircase, the lightning rod on the roof, calculation according to the set of completed positions . | komplet | 1 |  |  |  | 0
29 | Procurement of materials, transport and assembly of contact moldings between demit facade on concrete elements of the main building and ventilated façade, calculation according to m1 built-in moldings. | m1 | 215.45 |  |  |  | 0
VII JOINERY WORKS
30 | Procurement, construction, transport and installation of fire doors F90, (one on evacuation staircase and the other in the northeast facade) light size 90/240 cm. Full, steel, gullwing fire doors equipped with standard fire-protecting hinges, fire-protecting profile with Eurocilline with 3 keys, fire-protecting strips, fire-protecting seal, fire-protecting stainless steel handle, one hydraulic automatic self-closing machine. Final treatment with electrostatic plasticity in tone according to the designer's choice in accordance with the standard color card. Submit the required fire resistance certicite of complience to the site. All work according to the description and scheme of the locksmiths from the project and with the consent of the designer. Calculation per piece, all completely. | pcs | 2 |  |  |  | 0
31 | Procurement, transport and installation of two aluminum windows with all necessary fittings on the annex on the northwest façade, dim. of windows 1200x1600 mm, windows with three-layer thermosolation glass, the price includes disassembly of existing windows. Calculation per piece of built-in locksmith . | pcs | 2 |  |  |  | 0
32 | Procurement, transport and installation of a ventilation grille located on the northeast façade, the price includes the dismantling of the existing one, calculation by piece. | pcs | 1 |  |  |  | 0
33 | Procurement, transport and installation of al.profile joinery on the northeast-back façade of the building, al.joinery is fixed without opening, the profiles are filled with security thermo-insulating matte glass. Calculation per m2 of built-in locksmiths. | m2 | 274 |  |  |  | 0
34 | Purchase of materials, transport and installation of tubular profiles 30 x 30 mm on the part of annex roof, which has AB ceiling for equalization of that part of the roof and one with INP construction, calculation per kg of steel frame construction of required height. | kg | 400 |  |  |  | 0
35 | Procurement of materials, transport and installation of tubular profiles 20 x 20 mm on the part of the roof of the annex which has an INP construction for equalization of that part of the roof and adjacent which has a higher level, calculation per kg of installed steel frame construction of the required height. | kg | 225 |  |  |  | 0
VIII TILING WORKS
36 | Supply, transport and installation of floor granite tiles.Dimesion of tiles is 60x60 cm thickness 10 mm. Ceramics is of I class, with rectified edge and matt surface, uniform appearance (V1), slip resistance R9, manufactured according to technology that meets ecological requirements (LEED, EcoLabel). Adhere ceramics with a flexible adhesive of the C2TE classification of renowned manufacturers in the shape of joint-to-joint The coated surfaces must be flat, joints must be precise, about 1 mm, the bond is normal in relation to the position of the walls.Fitted tiles shall be cleared with sawdust. Choice of collection and type in consultations with the designer. The price includes the purchase, transport and placement of tiles together with glue and joints filler. Calculation per m2 | m2 | 177 |  |  |  | 0
37 | Supply, transport and installation of floor granite plates, 60x60 cm tile, thickness 10 mm. Ceramics are I class, with rectified edge and matt surface, uniform appearance (V1), slip resistance R9, manufactured according to technology that meets ecological requirements (LEED, EcoLabel) Adhesive ceramics with flexible adhesives of the C2TE classification of renowned manufacturers in the shape of joints on the joint. The coated surfaces must be flat, fuzz precise, about 1 mm, the style is administratively in relation to the position of the walls. Fit tiles and clean with sawdust. Choice of collection and type in consultations with the designer. The price includes the purchase, transport and placement of tiles together with glue and gypsum. Calculation per square meter. " "Procurement of materials and installation of 10 cm tile from granite ceramics. Dimension of plinth is 60x15 cm. Ceramics is of 1st class Adhere ceramics with the flexible adhesive of the C2TE S1 (S2) classification of renowned manufacturers in the style of joint-onthe-jointn the joint. The coated surfaces must be flat, joints must be precise and minimal. Fitted tiles should be pointed and cleaned with sawdust. The plinth must be from the same collection as the floor tile to which it is placed. Choice of collection and type in consultations with the designer. The price includes the purchase, transport and placement of tiles together with glue and joints filling. Calculation per m1. | m1 | 165.4 |  |  |  | 0
| IX PAINTING WORKS | [5 empty] | 0
38 | Purchase of materials, transport and painting with silicate concrete color of the evacuation concrete staircase, visible side walls and slopes of stairways, primar/undercoat applied, surface prepared in respect to the technology of the manufacturer, coating is in two hands. Color chosen by the designer. The price includes purchase, transport and unloading of materials and work scaffold. Calculation per square meter, fully executed positions. | m2 | 138 |  |  |  | 0
X FACADE
39 | Purchase of material, transport and making DEMIT facade (on the part of the annex, the concrete elements of the main building, on the pillars on the northeast facade where the locksmith works are located), with mineral mineral wool Insulation of the following composition: adhesive mortar; mineral wool d = 15 cm; textile glass mesh; vapor permeable coating; precious waterproof mortar granulation according to the request of the Investor. Perform the work in accordance with the manufacturer's instructions and details. This position includes the purchase, transport and installation of all materials. | m2 | 512 |  |  |  | 0
XI FACADE ALUMINIUM
40 | Purchase of materials, transport and production of aluminum ventilating facade in the southeast part with semi-hard pressed stone wool thickness 100mm + vapor-permeable-waterproof foil and aluminum finish d = 1.5mm on aluminum substructure, according to the manufacturer's system instructions, the price is calculated and use of the scaffold. Calculation per m2 of installed facade. | m2 | 1050 |  |  |  | 0
41 | Purchase of materials, transport and production of aluminum ventilating facade with semi-hard pressed stone wool 100mm thickness + water-vapor permeable foil and aluminum finish d = 1.5mm on aluminum substructure. In the northwest (about 50% of the facade is tape-cut by 16 cm, so longer distancers are needed, the ventilating layer will be wider). In all, according to the instructions of the system manufacturers, the price is calculated and the use of scaffolding. Calculation per m2 of built-in facades. | m2 | 350 |  |  |  | 0
42 | Purchase of materials, transport and production of decorative plaster around the entire building at a height of h = 0.50 m, type silicate-silicon waterproof, parapropic, preparation must be done with stirodurum of certain thickness, then glue with fiberglas mesh, the primar/undercoat and then the final layer of granulation according to the choice of the Investor. Calculation per m2 of treated surface. | m2 | 150 |  |  |  | 0
| XII ROOFING WORKS | [5 empty] | 0
43 | Purchase of materials, transport and covering the roof above the sports arena, aliminium sandwich tin panels with filling of mineral d = 100,00 mm from the existing substructure, panels, attested to fire protection, joints and all penetrations on board must be arranged in accordance with the technical sheets of the manufacturer giving the warranty period for their product. Panel color by the choice of Investor, the price includes scaffolding or use of mobile platforms, calculation per m2 of covered roof. | m2 | 2200 |  |  |  | 0
44 | Purchase of materials, transport and installation of trapezoidal sandwich tin sheet with insulation on the part above the annex, calculation per m2 of covered surface. | m2 | 45 |  |  |  | 0
45 | Purchase of materials, transport and roof covering above the annex with AB ceiling, aluminium sandwich tin panels with filling of mineral thickness = 80,00 mm from the existing substructure, panels, attested to fire protection, couplings and all breakthroughs on the roof to be consulted in cooperation with the technical sheets of the manufacturer that gives the warranty period for their product. Panel color by the choice of the Investor, the price includes the installation of the scaffold, the installation of a metal substructure which does not include the inclination of the new roof cover will lead to a slope of 2 ° to the existing corners, calculation per m2 of covered roof. | m2 | 558 |  |  |  | 0
46 | Purchase of materials, transport and covering of the roof above an annex that has a grid of INP steel profiles, aluminium sandwich tin panels with mineral filler thickness = 80,00 mm with existing substructures, panels , attested to fire protection, joints and all penetrations on board must be arranged in accordance with the technical sheets of the manufacturer that gives the warranty period to their product. Panel color by the choice of the Investor, the price includes scaffolding, the installation of a metal substructure which does not include the inclination of the new roof cover to the slope of the higher deck , calculation per m2 of covered roof. | m2 | 87.5 |  |  |  | 0
XIII MACHINERY
47 | Delivery and installation of heat pump air-water for outdoor installation, with device housing of galvanic protected steel, the following minimum characteristics: Cooling capacity 12° C/7°C 313.6 kW Total power 119,7 kW EER 2,62 ESEER 3,85 Water flow 54057 l/h Pressure drop 33 kPa Total input current (cooling) 207 A Heating capacity 4°C /45°C 344,7 kW Total input power 112.3 Kw Minimum COP 3 Heating energy class Eurovent B Total input current (heating) 197 A Compressors / circuits 4/2 Hydro module - cent. pump power: P= 2,2 kW Anti-vibration support Remote panel with the following remote interface: turn ON/OFF mode summer/winter status WORK status MALFUNCTION The interface must be realized with classical signals (NOT THROUGH MAGISTRALE) | pcs | 2 |  |  |  | 0
48 | Delivery and installation of air-conditioning chamber capacity 33000 m3 / h, for injection and extraction of air from the sports hall space, the following minimum characteristics: Location indoor Delivery in parts AHU ends outdoors in standard color (RAL 7035) Range of options is excluded AHU configuration double (opposite) Total weight (each) kg 3819 Radiated objects SVL) dB (A) 73 ErP identification code NRVU / BVU SFPe kJ / m3 3.52 SFPv kJ / m3 3.35 OUTPUT DATA Air volume m³ / s 9.17 Construction of the GP080 case 60 mm internal sheet metal galvanized 0.80mm Isolation glass fiber 20-30 kg / m3 External sheet metal PUR-PA painted galvanized steel 0.80mm Unit speed m / s 2.49 SFPe kJ / m3 1.55 SFPv kJ / m3 1.51 INPUT PLENUM Type of diffuser by pulling Fan Qty 1 Installed engine power 15 kW Air volume 9.17 m3 / s External static pressure Pa 500 Internal static pressure Pa 443 Static pressure ISP + ESP Pa 943 Systemic effect Pa 94 Extra static pressure Pa 0 Total static pressure Pa 1037 Dynamic pressure Pa 77 Total pressure Pa 1114 Fan speed rpm 1232 Max. rotary valve rpm 1285 Efficiency% 82 Fan power kW 12.46 Supplements Measuring points of the input cone Individual flexible connection RECUPERATOR Winter conditions Exhaust air on °C/%RH 22.0 / 40 Exhaust pressure drop Pa 315 Exhaust air off °C/%RH 1.9 / 100 Summer conditions Exhaust air on °C/%RH 25.0 / 50 Exhaust pressure drop Pa 315 Exhaust air off °C/%RH 31.9 / 33 FILTER Filter type Panel (Synthetic) Withdrawal method Side Class M5 Test method Weight arrestance acc. EN779 Initial pressure drop Pa 169 Designed pressure drop Pa 240 Final pressure drop Pa 310 Filter length mm 48 Filter frame material galvanised Filters 592x592 Qty 6 437x592Qty 2 287x592Qty 3 287x437Qty 1 | pcs | 1 |  |  |  | 0
49 | Delivery and installation of automatic of air-conditioning chamber with a minimum capacity of 33000 m3/h and following characteristics: Microprocessor regulator for complete climate chamber Device for manual el. valve control RDV 2 Electromotor three-way regulation valve, flanged NP 16, DN 65 Electromotor three-way regulation valve, flanged NP 16, DN 40, Kvs = 25 m3/h, for water Electromotor drive blinds of waste air, on/off control Power supply 24VAC. Operation ON/OFF. Detection of open position. Starter of a blind of fresh air: power supply 24VAC. Closing with spring. Operation ON/OFF. Detection of open position. Power supply 24VAC. Operation 0...10VDC. Service switches for both fans, as well as light chamber. Launcher of the blind of the recuperator: Power supply 24VAC. Operation 0...10VDC. Launcher of the mixing valve of cooling the air-conditioning chamber from the warm. pumps 7C Power supply 24VAC, operation 0...10VDC. Launcher of the mixing valve of heating the air-conditioning chamber from the warm. pumps 45C Power supply 24VAC, operation 0...10VDC. Launcher of the mixing valve of the heating of the air-conditioning chamber from the boiler room 90/70C: Power supply 24VAC, operation 0...10VDC.Automatic FD dumper with electric switch Location is shown in the graphic documentation ( 2 pcs ) In case glycol fluid is used, it is needed to place a board/flat heat exchanger (pcs 1) between the buffer and bus bar so the glycol wouldn’t get into the existing heating system. | set | 1 |  |  |  | 0
50 | Delivery and installation of equipment for heat substation with heating and cooling: temperature of hot water: 40˚C/45˚C complete pipe fitting, shut-off valves, measuring and bleeding fittings, busbar and three-hole splitter, Ø 273 mm control circuit for warming temperature setting of consumable water, composed of three-way split valves with electric drive, dimensions DN125 (Qty 2), circulation pumps of the following characteristics: P = 1100 W, n = 2150-2800 rpm (Qty 3) circulation pumps of the following characteristics: P = 1800 W, n = 2450-2900 rpm (Qty 1)expansion vessel volume V = 500 l security valve DN40PN16 double valves DN20 (Qty 2) non-return valves DN150 valves (Qty 8) sloping control valves DN125 (Qty 2) and DN80 (Qty 1) headers of impurities DN125 (Qty 2) | set | 1 |  |  |  | 0
51 | Review and cleaning of existing channels for air intake. Inspect the inside of the channel with a camera. Channel dimensions: 1000x1200 mm 40 m 1000x1000 mm 12 m 900x1000 mm 35 m 500x700 mm 250 m | lump sum | 1 |  |  |  | 0
52 | Repair of existing channels for air intake. Inspect the inside of the channel with a camera. Replacement of visible sheet metal channels surface up to 40 m2. In the price is calculated connecting, sealing and auxiliary mounting material in case of need for channel rehabilitation in some areas. Channel dimensions: | m | 10 |  |  |  | 0
|  | m | 4 |  |  |  | 0
|  | m | 10 |  |  |  | 0
|  | m | 70 |  |  |  | 0
56 | Review and cleaning of an existing air pull-out channel below the stands. Inspect the inside of the channel with a camera. In the price is calculated connecting, sealing and auxiliary mounting material in case of need for channel rehabilitation in some areas. | lump sum | 1 |  |  |  | 0
57 | Repair of an existing air pull-out channel below the stands. Inspect the inside of the channel with a camera. In the price is calculated connecting, sealing and auxiliary mounting material in case of need for channel rehabilitation in some areas. | kg | 30 |  |  |  | 0
58 | Review and cleaning of an existing air pull-out channels above the stands section. Inspect the inside of the channel with a camera. In the price is calculated connecting, sealing and auxiliary mounting material. | lump sum | 1 |  |  |  | 0
59 | Repair of an existing air pull-out channels above the stands section. Inspect the inside of the channel with a camera. In the price is calculated connecting, sealing and auxiliary mounting material. | kg | 30 |  |  |  | 0
60 | Review and cleaning of an existing masonry channel for pulling out air. The channel is located below the floor level of the annex part of the sports hall and it serves to take air to the substation. Total length of the existing channel is about 35 m and the dimension of the channel in the widest part is 1.4 m. Complete channel route through the corridor is inaccessible and therefore it is necessary to carry out construction work on opening of the channel (breaking of tiles and concrete slabs) on the floor of corridor (area of about 80 m2). In addition to these works, it is necessary to foresee removing of the entire floor from the edge of the channel to the walls and after channel repair make the preparation of the substrate for installation a new floor in the entire corridor. The price includes the removal of the construction waste at the landfill. | lump sum | 1 |  |  |  | 0
61 | Repair of an existing masonry channel for pulling out air. After the opening of the canal with supervision for construction works, determine the condition of the walls and the bottom of the channel and, if necessary, rehabilitate them with partitioning or concreting. For channel closing needs pour reinforced concrete ring beam into which is positioned the L carrier on the channel scope. L carrier is included in the price. The price includes the removal of the construction waste at the landfill. | lump sum | 1 |  |  |  | 0
62 | Performing works on closing the masonry channel for extracting air. Previously cleaned and repaired channel cover with mobile boards made in a way that visually fit into the whole. Plates up to 120 kg set to the L profiles that need to be fixed to the edges of the channel. The final material should be the same as the material used to pave the corridor below which there is no channel. Ensure complete suction of the channel. Ensure the lifting grips on plates. Tiles must be of I class quality, anti-slip, thickness of 1 cm. | m2 | 90 |  |  |  | 0
63 | Procurement, installation and pavement works in the part of the corridor in which works on the masonry channel for extracting air were made. Tiles must be of I class quality, anti-slip, thickness of 1 cm. The price includes works of the construction of bottom concrete ring 10 cm high. | m2 | 30 |  |  |  | 0
64 | Dismantling, purchase and installation of new air extraction grilles made of anodized aluminium in natural colour, for installation on wall with 1 row of adjustable blades parallel to the first mentioned dimension. The price includes minor construction works Dimensions of grilles: 600x300 mm | pcs | 14 |  |  |  | 0
65 | Dimensions of grilles:500x300 mm | pcs | 13 |  |  |  | 0
66 | Dismantling, purchase and installation of round ceiling diffuser made of anodized aluminium in natural colour with round concentrical fixed blades. Diameter of the diffuser Ø 440 mm. All necessary tin works are included in the price. | pcs | 12 |  |  |  | 0
67 | Dismantling, purchase and installation of metal jet nozzle for connection to flexible duct/ round sleeve/ the side of rectangular air duct/ the side of round air duct, with adjustable head to regulate the air stream direction. The head is moved upwards (cooling) or downwards (heating). Diameter Ø 440 mm and range up to 10 m. All necessary tin works are included in the price. | pcs | 24 |  |  |  | 0
68 | Removal of the old ones, purchase and installation of the new multileaf air flow controllers with few blades made of galvanized steel sheet for installation in rectangular air ducts. Manualy operated. Included all costs of tin works and elements. Dimensions: 1000x1200 mm 1000x1000 mm 1000x900 mm 1000x900 mm | pcs | 4 |  |  |  | 0
69 | Purchase and installation of seamless steel tubes for connecting the air-conditioning chamber and heat pump, as well as for the distribution of the installation and connection in the substation, diameter and dimensions according to the graphic documentation. with all For joint, sealing, auxiliary material for assembly and all necessary fittings is taken Dimensions: DN32 | m | 2 |  |  |  | 0
70 | DN40 | m | 4 |  |  |  | 0
71 | DN50 | m | 2 |  |  |  | 0
72 | DN80 | m | 2 |  |  |  | 0
73 | DN125 | m | 120 |  |  |  | 0
74 | DN150 | m | 10 |  |  |  | 0
75 | Anticorrosive protection of steel pipes with protective coating in two layers | m2 | 12 |  |  |  | 0
76 | Purchase and installation of the thermal insulation of hot and cold water pipelines with hoses made on the basis of synthetic caoutchouc with steam barrier, self-extinguishing, fire resistance class "B1" complete with assembly material | m2 | 380 |  |  |  | 0
77 | Purchase and installation of brass ball valves at the air-conditioning chamber connections and at the heat pump connection. Dimensions: DN32 | pcs | 2 |  |  |  | 0
78 | DN40 | pcs | 4 |  |  |  | 0
79 | DN50 | pcs | 2 |  |  |  | 0
80 | DN80 | pcs | 2 |  |  |  | 0
81 | Purchase and installation of hot water tank volume 3m3, height limit up to 3 m, with all necessary and appropriate connections for heat pumps and existing hot water reservoir. Predict the two temperature probe pockets on the side. One at 20% in height, the other at 80% in height. Pockets need to be made of stainless steel, internal diameter 6mm, depth 300mm. The process connection of the projected probes is R1". Provide the necessary evidence of quality. In case that it is not possible to install the original product of the approved manufacturers, it is necessary to provide all supporting documentation for proving the quality of materials and works on the production of hot water tank. | set | 1 |  |  |  | 0
82 | Production of reinforced concrete base dimensions 6 x 10 m, height 0.15 m with all necessary preparatory and finishing works and procurement of materials. The position of the stand is shown in the graphic documentation (situational plan). Installation of the pipe through which the electrical cables of the heat pump installations will be installed. Construction of a 6 x 10 x 2 m metal barrier for heat pumps with doors for access to heat pumps. Creation of a canopy for electric cabinets of 2 m2. When laying the foundations for the base, the basic grounding should be foreseen. Foreseen basic grounding for heat pumps and electric cabinets. In coordination with the responsible electric contractor, connect the ground earthing with earthing placed in the trench of the power cable. | set | 1 |  |  |  | 0
83 | Earthwork (trench) to a depth of 2 m, demolishing the exterior wall of the substation so that the existing dismantled equipment can be removed and introduced new equipment. Afterwards returning to original condition, with all necessary preparatory and final works and procurement of materials. | set | 1 |  |  |  | 0
84 | Preparatory finishing works: Develop a plan of preventive measures for the respective construction site | set | 1 |  |  |  | 0
85 | Installation and disassembly of the scaffold for the execution of works on ventilation installation within the hall at a height of 14 m | set | 1 |  |  |  | 0
86 | Dismantlement of the existing equipment in the substation and hall, and waste disposal up to 5 km | set | 1 |  |  |  | 0
87 | Installation of thermostatic installations and equipment, testing, adjustment of operating parameters and trial | set | 1 |  |  |  | 0
88 | Minor construction work on breaking openings (5m2) | set | 1 |  |  |  | 0
89 | Project of the constructed object | set | 1 |  |  |  | 0
90 | Creation of a geodetic survey of the installed installations and concrete platform on which heat pumps are installed | set | 1 |  |  |  | 0
91 | Regulating the air current on the channels and air diffusers, and nozzles and channels. Commissioning | set | 1 |  |  |  | 0
92 | Preparatory finishing works | set | 1 |  |  |  | 0
XIV ELECTRIC INSTALLATION AND AUTOMATION
1. ELECTRIC CABINETROAAND EQUIPMENT FOR ELECTRIC CABINET, PLC CONFIGURATION, PANEL
Purchase of all necessary equipment, workshop design, connection and internal testing of electromechanics. Delivery of the cabinet to the construction site and placement on the specified place. The cabinet consists of the following components:
| Automatics cabinet Compact cabinet, 1 door, 2000x1000x400mm (HWL),IP55. Metal with a mounting plate, IP55 | pcs | 1
| Concrete base for electric cabinet | pcs | 1
| A pocket for documentation A4 | pcs | 1
| 3-pole switch, rated voltage 690VAC, rated current 100A, breaking capacity 25kA, with microprocessor protection unit 100A, with 200 / 240VAC trip switch, with auxiliary position signaling contact | pcs | 1
| distribution block 125A | pcs | 1
| Cabinet lights | pcs | 1
| Power outlet - service, within the cabinet of the DIN rail | pcs | 1
| Presence control, asymmetry and phase sequence | pcs | 1
| Two-pole connector, OG, for sideways mounting on the cabinet | pcs | 1
| Fuse 16A - single-pole | pcs | 1
| Fuse6A – three-pole | pcs | 1
| Fuse 10A – one-pole | pcs | 2
| Fuse 6A – two pole | pcs | 1
| Aut. Fuse 4A/C/2 pole | pcs | 1
| Aut. Fuse 2A/C/2 pole | pcs | 5
| Aut. Fuse 6A/C/1 pole | pcs | 3
| Aut. Fuse 2A/C/1 pole | pcs | 1
| Power supply 400VAC/ 24VDC 5A | pcs | 1
| Power transformer 400/24VAC 250VA | pcs | 1
| Motor protective relay range 4-6.3 A.The switch should be in accordance with the selected Pump from Mechanical Project. | pcs | 1
| "Motor protection relay range2.5-4 AThe switch should be in accordance with the selected Pump from Mech. Project. " | pcs | 6
| "Motor protective relay range 24-32A The switch should be in accordance with the selected ventilator from Mech. Project. " | pcs | 1
| Motor protective relay range 30-40A The switch should be in accordance with the selected suction fan from Mech. Project. | pcs | 1
| Auxiliary contacts for motor protection switches | pcs | 9
| Contact relays 12A, 24VDC | pcs | 7
| Relays 1NC/NO, 24 VDC with a counter diode and a stand | pcs | 21
| Relay 4NC/NO, 24 VDC with a counter diode and a stand | pcs | 1
| Relay 1NC/NO, 24 VDC with a stand | pcs | 1
| Switch (button) NOTAUS | pcs | 1
| Greeen signal lamp 24VDC | pcs | 2
| Red signal lamp 24VDC | pcs | 1
| Small material inside the cabinet: clamps, terminal markings, device markings, shimmering wire, ducts, DIN rails,Cable ends,pedals, screws, grips, ties, labels and other small non-specified material Inside the cabinet | set | 1
| PLC with IO cards suitable for receiving the signal of all specified equipment in the field. Minimum number of signals: DI: 54 DO: 26 AI: 10 AO: 6 | pcs | 1
| GSM modem suitable for the connection with the chosen PLC. | pcs | 1
| Ethernet Switch least 5 ports, copper, power supply 24VDC Mounted on DIN rail. | pcs | 1
| Panel 10“, touch, color, With the ability to archive data. The panel must be suitable for connection to the selected PLC. | pcs | 1
| Delivery and installment of anti panic safety set of lights, LED or for fluo pipe 2x8W, with independent work for 3h. IP 40 with mark – ARROW | pcs | 3 | 3
93 | TOTAL ELECTRIC CABINETGOA,EQUIPMENT FOR ELECTRIC CABINET, PLC CONFIGURATION, PANEL | set | 1 |  |  |  | 0
2. ELECTRIC CABINET FOR SMALL PANEL, PANEL
Purchaset of all necessary equipment, workshop design, connection and internal testing of electromechanics. Delivery of the cabinet to the construction site and placement on the specified place. The cabinet consists of the following components:
| Box for small panel by thechamber: On the wall metal cabinet, 1 door, 400x400x210mm (HWL) with mounting plate. IP54 | pcs | 1
| Switch (button) confirmation | pcs | 1
| buzzer 24VDC | pcs | 1
| Green signal lamp 24VDC | pcs | 1
| Red signal lamp 24VDC | pcs | 1
| Panel 7“ Touch, color. The panel must be suitable for connection to the selected PLC. | pcs | 1
| Small material inside the cabinet: clamps, terminal markings, device markings, shimmering wire, ducts, DIN rails,Cable ends,pedals, screws, grips, ties, labels and other small non-specified material Inside the cabinet | set | 1
94 | 2. TOTAL ELECTRIC CABINET FOR SMALL PANEL, PANEL | set | 1 |  |  |  | 0
3. FIELD EQUIPMENT
| Channel fire detector Setting range 20-110°C. Set value of about 60°C. 1NC / NO. Automatic reset. | pcs | 1
| Channel fire detector Setting range 20-110°C. Set value of about 60°C. 1NC / NO. Automatic reset. | pcs | 1
| Frost sensor capillary Length of capillary 6m Setting range -5 ... 15°C. Set value of about 5°C. 1NC / NO. Automatically reset. | pcs | 1
| Differential pressure switch for detecting the operation of the insert fan Setting range 20..300Pa. Set value around 100Pa. 1NC / NO. With mounting set. | pcs | 1
| Differential pressure switch for exhaust fan operation detection Setting range 20..300Pa. Set value around 100Pa. 1NC / NO. With mounting set. | pcs | 1
| Differential pressure filter for roughness detection. Setting range 20..300Pa. The setpoint is about 150 Pa. 1NC / NO. With mounting set. | pcs | 1
| Differential pressure detection filter for fine filtering. Setting range 30 ... 500Pa. Set value around 300Pa. 1NC / NO. With mounting set. | pcs | 1
| Differential Pressure Detection Detector Receptor-fresh v. Setting range 30 ... 500Pa. Set value around 300Pa. 1NC / NO. With mounting set. | pcs | 1
| Differential Pressure Detection Detection Sensor v. Setting range 30 ... 500Pa. Set value around 300Pa. 1NC / NO. With mounting set. | pcs | 1
| External temperature sensor with Atmospheric shield and facade fittings. Power transm. 24V AC / DC (2-wire or 4-wire). Output 0 ... 10VDC or 4..20mA. Range -25 ... 50°C or broader. The transmitter can be separated from the probe. | pcs | 1
| Channel temperature sensor. Power supply 24VAC / DC. (2-wire or 4-wire). Output 0 ... 10VDC or 4..20mA. Range 0 ... 50C or broader. The transmitter can be separated from the probe. | pcs | 1
| Channel temperature sensor. Power supply 24VAC / DC. (2-wire or 4-wire). Output 0 ... 10VDC or 4..20mA. Range 0 ... 50C or broader. The transmitter can be separated from the probe. | pcs | 1
| Room temperature sensor with mounting kit on the wall. Power supply 24VAC / DC. (2-well or 4-well). Output 0 ... 10VDC or 4..20mA. Range 0 ... 50C or broader. The transmitter can be separated from the probe. | pcs | 1
| Room temperature sensor with mounting kit on the wall. Power supply 24VAC / DC. (2-well or 4-well). Output 0 ... 10VDC or 4..20mA. Range 0 ... 50C or broader. The transmitter can be separated from the probe. | pcs | 1
| Temperature sensor for heat storage. Temperature probe Pt100. Stainless steel probe, Fi6mm, L = 300mm. Thread R 1 ". Power supply 24VAC / DC. (2-wire or 4-wire). Output 0 ... 10VDC or 4..20mA. Range 0 ... 100C or broader. The transmitter can be separated from the probe. CAUTION: Align the process connector and dimensions with the supplied pocket. The pocket comes as part of the heat storage. | pcs | 1
| Temperature sensor for heat storage. Temperature probe Pt100. Stainless steel probe, Fi6mm, L = 300mm. Thread R 1 ". Power supply 24VAC / DC. (2-wire or 4-wire). Output 0 ... 10VDC or 4..20mA. Range 0 ... 100C or broader. The transmitter can be separated from the probe. CAUTION: Align the process connector and dimensions with the supplied pocket. The pocket comes as part of the heat storage. | pcs | 1
| Differential pressure sensor/ 0…2.500Pa, 0...10V, 24 VAC/DC. Mounting set: L tube for air line | pcs | 1
| Differential pressure sensor/ 0…2.500Pa, 0...10V, 24 VAC/DC. Mounting set: L tube for air line | pcs | 1
| Flow switch for heatpump | pcs | 1
| Flow switch for heatpump | pcs | 1
| Frequency regulator for insertion fan specified in mechanical projects. Orientation data P = 15kW, In = 29.8A. The frequency regulator should have the possibility of an interface: analog (0..10VDC or 4..20mA) and digital command and statuses RAD and ALARM. Local display. Mounting in air conditioning chamber,IP55. | pcs | 1
| Frequency regulator for insertion fan specified in mechanical projects. Orientation data P=18.5kW, In= 34A. The frequency regulator should have the possibility of an interface: analog (0..10VDC or 4..20mA) and digital command and statuses RAD and ALARM. Local display. Mounting in air conditioning chamber,IP65. | pcs | 1
| markings of equipment of stainless material, marking Embedded in the tile | pcs | 1
95 | 3. TOTAL OF FIELD EQUIPMENT | set | 1 |  |  |  | 0
4. CABLES AND CABLE DIVISION OF AUTOMATICS AND EMP
Purchase of all necessary equipment, delivery to the construction site, Installation of the rack, Installation of the instrumentation. Cable laying, cable checking, connecting cables at both ends. Cable marking and instrumentation Checking installations. Treatment by remarks in the warranty period. This position also includes connecting all actuators, pumps and fans! Installation of pumps and actuators is in the machine compartment.Cables outside the cabinet are in protection pipes attached by screw bolts.Logistics costs. Maintenance of construction sites.
| cable LiHCH 3x0,75 | m | 220
| cable JH(St)H 1x2x0.8 | m | 80
| kabl JH(St)H 2x2x0.8 | m | 40 | 40
| cable JH(St)H 4x2x0.8 | m | 25
| cablel N2XH 4x2.5 | m | 100
| cable N2XH 3x1.5 | m | 70
| Cable N2XH 4x16 | m | 15
| cat5e | m | 10 | 10
| Cable carrier with the following features: Two parallel NNK REGALA 50x100 with lids and suitable mountings partly on the ceiling, partly on the wall. Locksmith processing of the REGALA should be such that the inside of the REGALA is not accessible to the rodents. | pcs | 12
| Cable carrier with the following features: Two parallel NNK REGALA 50x50 with lids and suitable mountings partly on the ceiling, partly on the wall. Locksmith processing of the REGALA should be such that the inside of the REGALA is not accessible to the rodents. | pcs | 25
| Cable carrier with the following features: NNK REGALA 50x50 with lids and suitable mountings partly on the ceiling, partly on thechamber. Locksmith processing of the REGALA should be such that the inside of the REGALA is not accessible to the rodents. | pcs | 15
| Angular elements, T bends, reducers, vertical coupling couplings for these REGALE – Set | set
| Metal plasticized hose Fi11 | m | 120
| Metal plasticized hose about Fi32 for fan cables | m | 4
| Cable labels (Cable labeled on both end) – SET | set | 1
| Power supply cabinet for automatics N2XH3x50+25 | m | 20
| Fuses NV00 125A with accompanying mounting accessories For installation in the existing distribution cabinet, and for the purpose of powering the cabinet automation | pcs | 3
| other small assembly materials for cable distribution (screws, helmets, buckles, boxes, ties, grips ...) | set | 1
96 | 4.TOTAL FOR CABLES AND CABLE DIVISION OF AUTOMATICS AND EMP | set | 1 |  |  |  | 0
5. POWER DISTRIBUTION CABINET FOE HEAT PUMPS
| Delivery and installation of free-standing Distribution cabinet RO-TP dimension 1000x1250x312mm of polyester reinforced with glass fiber, halogen-free self-extinguishing, UV-resistant, in the degree of protection IP 66 mounted on a concrete foundation, bottom edge at a height of 0.6m from the base, with bottom feeders through polyethylene pipes and with the following equipment included in the single-pole scheme: pcs | pcs | 1
| Copper bus bar (30x10x2000)мм | pcs | 1.5
| three pole copper bus bar carrier | pcs | 2
| end plate three pole copper bus bar carrier | pcs | 2
| 2 pole carrier N and PE bus bar | pcs | 2
| three pole dashboard with lid, to connect the power cable to the copper bus bar | pcs | 1
| connection terminals for connecting N and PE conductors to copper bus bars | pcs | 2
| connection terminals 16-120mm2 for connecting N and PE conductors to copper bus bars | pcs | 6
| connection terminals 1.5-16mm2 for connecting N and PE conductors to copper bus bars | pcs | 10
| Compact switch,MC3,3p,In=630A,50kA, protective units AE | pcs | 1
| Adapter for installation of MC3 on 60mm bus bar, up to 630A , installation on bus bar 30x10mm, with cover for adapter | pcs | 1
| adapter for single-pole automatic circuit breakers (4 pcs.), with two adjustable DIN rails | pcs | 6
| Mounting bracket (DIN rail high) non-perforated L = 2m | pcs | 1
| Mounting bracket DIN flat H50 | pcs | 2
| single pole protection switch 32A, characteristics C, for mounting on DIN rail with breaking power 10kA | pcs | 3
| single pole protection circuit breaker 16A, characteristic C, for mounting on DIN rail with interrupted power 10kA | pcs | 9
| single pole protection switch 10A, characteristic C, for mounting on DIN rail with breaking power 10kA | pcs | 3
| line clamps (terminals), DIN rail mounting, beige color, for conductors up to 16mm² | pcs | 10
| line clamps (terminals), for DIN rail mounting, gray color, for conductors up to 6mm² | pcs | 40
| Delivery and installation of single-phase alternating current socket, 250V / 16A with mounting on DIN rail. | pcs | 1
| Delivery and installation of three-phase OG socket, 3x230 / 400V / 16A with mounting on the appliance plate. pcs | pcs | 1
| Delivery and installation of three-phase industrial socket, 3x230 / 400V / 32A with mounting on the appliance plate. pcs | pcs | 1
| Delivery and installation lights in the cabinet with switch pcs. | pcs | 1
| End plate for line clamp pcs | pcs | 2
| End fixing clamp for line clamp pcs | pcs | 1
| Three pole NV00 seperator for 60mm bus bar system, installed on a bus bar 30x10mm | pcs | 1 | 1
| three pole NH2 seperator 400A for 60mm bus bar system, installed on a bus bar 30x10mm | pcs | 2 | 2
| Three pole NH3 seperator 630A for 60mm bus bar system, installed on bus bar 30x10mm | pcs | 1 | 1
| NV00 high capacity switch strength160A,characteristics gG. | pcs | 3 | 3
| NH2 high capacity switch strength 315A, characteristics gG. | pcs | 6 | 6
| NH3 high capacity switch strength 630A, characterisitics gG. | pcs | 3 | 3
| Contactorr AC3/400V, 4kW, 3P+NO+NC, 230Vac | pcs | 3 | 3
| Auxilery relay 5A/250V, 4NC/NO, namotaj 230Vac | pcs | 3 | 3
| Motor protection clutch 4,3A with an auxilery contact | pcs | 2 | 2
| line terminals, for installation on DIN rail, grey, for conductor up to 2.5mm² | pcs | 15 | 15
| Delivery and installation of complete cam switch, 2P, 20A with installation on DIN rail. | pcs | 2 | 2
97 | 5. TOTAL 5. POWER DISTRIBUTION CABINET FOE HEAT PUMPS | set | 1 |  |  |  | 0
6. LINE FOR THERMAL PUMP POWER SUPPLY
| Combined (machine and manual) earth excavation of the 4th category for laying a power cable, measuring 0,4mx0.8x210 m. The cable is laid partially along the route of an existing balloon hall cable, mainly on a grassy surface. After laying the cable and grounding tape, the trench is filled in layers and tramped . m3 | m3 | 210
| Production of concrete base for RO-TP, on the edge of the concrete plateau (on which heat pumps are installed). The foundation is moved from the edge of the plateau of 0.2m and it is 0.6m high, and the other dimensions are smaller than the width and depth of RO-TP for 2cm (0.98k1.248) m, so the water doesn't get under it. The foundation is anchored for the concrete plateau. Predict 4 anchors M10 placed in concrete (threaded rods) so that they are located at the ends of the imaginary rectangle dimensions (0.86k1.236) m, centimeterimetrically placed in relation to the upper surfaces of the base. These anchors (M10) exit from the base 40mm in relation to the upper surfaces of the base. Before filling the concrete, drill the plateau to get the opening of the corresponding diameter for the introduction of PE pipe into the foundation. Place the appropriate PE (polyethylene) pipes before filling in concrete and fasten them so that they are symmetrically grouped in the first 2/3 of the depth of the cabinet (viewed from the door of the cabinet). Apart from the necessary, also provide for three backup cables. Place through the concrete grounding wire. | pcs | 1
| Delivery and installation of the XP00 2x(4x120) mm2 for the supply of heat pumps, from RO-TS to the distribution box RO-TP. | m | 230
| delivery and installation of the XP00 4x120 mm2 for the supply of heat pumps from the distribution cabinet RO-TP. m | m | 26
| Isporuka i montaža signalnog kabla XP00 14x1,5 mm2 ili odgovarajući, za vezu između toplotnih pumpi i novog razvodnog ormana (RO-TP).Delivery and installation of signal cable XP00 14x1,5 mm2 or suitable, for connection between heat pumps and a new control-cabinet (RO-TP) in the sports hall. | m | 20
| Delivery and installation of mechanical protection of cables that are laid on concrete plate-base for heat pumps. Mechanical protection is performed using Ω profiles made of galvanized steel sheet 2mm thick, of the corresponding dimensions. m | m | 10
| Delivery and laying of the caution tape 30cm above the cables, laid in the trench. m | m | 270
| Delivery and installation of galvanized steel strips of 25x4mm cross-section with heat pump connection cable from RO "balloon hall" to RO-TP, so that the cable and tape in the trench are spaced apart. The tape is laid out from the balloon halls distribution box to the RO-TP. | m | 125
| Delivery and installation of galvanized steel strips of cross-section 25x4mm into the foundation of the concrete plate on which heat pumps are installed. Tape at each length meter weld for reinforcement (reinforcing mesh). Provide excerpt of this earth connection to heat pumps, as well as connect this grounding device to a grounding device fitted with a power cable. | m | 125
| Delivery and installation of a crossing piece for connection of the balloon hall grounding and the new grounding, as well as for the upgrading of the new tape. All joints must be applied with anti-corrosion protection. pcs | pcs | 8
| Delivery of small unspecified material and work. | lump sum | 1 | 1
| Delivery and installation of signal cable XP00 24x1,5 mm2 or suitable, for the connection between the new control cabinet (RO-TP)and automatics control cabinet (ROA) in sports hall. | m | 40 | 40
| Delivery and installation of signal cable XP00 3x1,5 mm2or suitable, for the connection between the new control cabinet (RO-TP)and 2 line switches. | m | 8 | 8
| Hand digging of the ground whole cross section 0.7m x 0.7m, depth 0.8m, for later development of foundation for outside light column. | m3 | 0.39 | 0.392
| development of foundation for outside light column, according to drawing. 1.7.7. u grafičkom delu dokumentacije. Temelj je dimenzija 0.7m x 0.7m x 0.8m. In the foundation installation of pipes Φ75mm, For cable entrance, anchor basket. Top coat of foundation must be evened out and flatand between the ancher plate columnand the foundation it is needed to put a rubber seal. | m3 | 0.39 | 0.392
| Delivery and installation of cable PP00 3x6mm2, from RO-TP, partly inside the poliethylen hose (or pipe) ø75 incorporated into the concrete base, with column . Pipe ø75 pput into the concrete base. | pcs | 1 | 1
| Deliverz and installation of Isporuka i ugradnja conical galvanized hexagonal column for lights height 4m, with anchor basket, equipped with a carrier RPO plate andattached plate/board RPO/FRA, lid opening with,grounding, screws for installation, PVC caps for achers, rubber cap for installation between the acher column plate and concrete foundation | pcs | 1 | 1
| Delivery nd installation of LED lights 50W/230V, IP66, (3000-4500)⁰K, with adapters for installation on columns | pcs | 1 | 1
98 | 6. TOTAL LINE FOR THERMAL PUMP POWER SUPPLY | set | 1
| 7. Repair of existing grounding system with change of parts |  |  | KOLIČINA | EUR/kom
99 | Delivery and replacement of the receiving system and the delivery lines with a galvanized steel strip of cross-section (20x3) mm with suitable backing, supports and connecting element | m | 280 |  |  |  | 0
| Delivery and replacement of the discharge lines with galvanized steel strip cross-section (20x3)mm with suitable carriers and connecting elements | lump sum | 1 | m |  |  | 0
| Delivery and assembling of cut pieces - joining elements for joining galvanized steel strip | lump sum | 1 | kom |  |  | 0
| Delivery and installation of joining elements for joining galvanized steel strips with horizontal gutters | lump sum | 1 | kom |  |  | 0
| Delivery and installation of mechanical protection of the earthing of the earthing, with the cleaning of the earthing of the earplugs and AKZ | lump sum | 1 | kom |  |  | 0
100 | "ENGINEERING WORKS IN THE WORKSHOP (90 inputs / outputs) Production and internal testing of PLC, OP program Examination of the electric cabinet in the workshop. Creating documentation of the performed works „ dokumentacija izvedenog objekta “Creating work instructions. " | lump sum | 1 |  |  |  | 0
101 | "ENGINEERING WORKS ON THE BUILDING Jobs of the responsible Contractor for works Jobs of the Safety Officer at Work Setting all devices, internal installation testing Commissioning of PLC, OP programs and functional testing of the system Training of users Treatment by remarks in the warranty period. Manipulative and logistics costs. | lump sum | 1 |  |  |  | 0
102 | Delivery and installation of thermal cables for vertical gutters in order to prevent ice to clog up the inside of gutter | m1 | 200 |  |  |  | 0
|  | TOTAL TENDER OFFER: |  |  |  |  | 0