# VOLUME 3

# TECHNICAL SPECIFICATIONS

1. SUMMARY TECHNICAL DESCRIPTION

The building under construction was designed in Zrenjanin and is located on plot number 7540 CM Zrenjanin I, in Dr Kornel Radulovic Street no 18. The plot has an area of 913 m2. The building is within the scope of the PGR "Southeast" plan in Zrenjanin (Official Gazette of the City of Zrenjanin No. 32/14). The building is designed as a business, number of floors(-1,B1 + GF + 1F). The site in question houses the family residential building No.1 and the auxiliary building No.2 which have been destroyed and self-ruined and  must be removed. Parts of the foundation of the building will be reconstructed. According to the General Regulation Plan "Southeast", the purpose of the whole building will change from residential to business.

Building 1- family residential building, on the plot, number of floors GF, BRGP = 123 m2

Facility 2- auxiliary building, on the plot, number of floors GF, BRGP = 52 m2

Building 3-auxiliary building, on the plot, number of floors GF, BRGP = 119 m2

Building 4- auxiliary building, on the plot, number of floors GF, BRGP = 79 m2

The building is functionally zoned so that the technical rooms are located in the basement. There is one entrance to the facility as well as one vertical communication (staircase). The approach and entrance to  to the building, as well as the flows of horizontal and vertical communications around and within the building, are clearly defined and levelled in importance.

The staircase vertical is at the base of the building so as to ensure smooth communication and easy movement through parts of the building. In the basement are designed: entrance halls, staircase vertical, technical rooms with an exhibition area where the used technologies are perceived , the accompanying office and the toilet. On the high ground floor there is a projected office space, with an archive, toilets and a kitchenette. There are offices, a meeting room, a toilet and a kitchen on the first floor .

Constructive assembly: the object is solved as two independent skeletal structures of the same number of floors.

Up-to-date materials are foreseen for the construction of the building, while rational construction will take into account the rational use of resources, energy and land, so that the new construction will be a quality improvement of the space, not its degradation. The interior walls are made of brick d = 12 cm. Finishing the interior walls is plastering and painting with distemper. In the kitchens, the walls are covered with ceramic tiles from the floor up to 150 cm in height, and in the toilets from the floor to the ceiling. The floors in the kitchens, bathrooms, staircases, in the auxiliary rooms in the basement, as well as in the hallways are made of ceramic tiles, and in the office spaces the floors are made of parquet. The facade joinery is aluminium, glazed with triple insulation glass. The interior joinery in the auxiliary and sanitary rooms is made of wood and MDF, painted with polyurethane varnish, while the doors of the offices are made of aluminium profiles, glazed with double glass.

The project envisages the construction of the building - energy efficiency centre, number of floors -1, B1 + GF + 1F, which consists of two structural units - a reinforced concrete main building and a steel structure of glass facade supports. The building is i base regular, rectangular in shape, with a foundation surface of approximately 175m2. The main building is designed as a multi-story construction of a static system of reinforced concrete frames, which are supported by solid reinforced concrete slabs. The columns are placed in orthogonal axes that follow the direction of the facade. The staircase is located along the facade of the building. Vertically, the building is designed on 3 levels with a roof structure consisting of 3 roof slabs, supported by reinforced concrete beams. The constructive heights of the rooms depend on the level at which they are located, so that we have a height of 311cm in the basement at the lowest level, 280cm on the ground floor, 280cm on the first floor, measured to the bottom of the roof structure and 570cm on the first floor measured from the top of the roof structure.

Indoor installations consist of heaters and pipe work. Three-pipe parapet fan coil units are provided as heaters. Dispositions of heating elements and piping are shown in the graphic documentation. Fan coil units operate in heating mode in winter and in cooling mode in summer. Hot air condensation occurs during the summer, due to its cooling, the condensate is discharged through the condensate network to the boiler room and from there to the sewer. The boiler room is located in the basement of the building.

Roads, water supply and sewerage

Roads

The connection to the public road is maintained from Dr. Kornel Radulovic Street via plot number 9648. Parking space is provided in front of the plot with four parking spaces, while two parking spaces are provided on the plot in question. Parking spaces in front of the lot will be constructed from pd raster cubes, and parking lot frames will be made of specially shaped raster in order to notice the separation of individual parking lots for passenger vehicles.

Sewage

Atmospheric sewage

Atmospheric water is drawn from the roof into vertical gullies through a sink with a heater and a basket, yard traps with cast iron frames and grilles are provided on the horizontal distribution and everything is collected into a lifting device.

As the distribution level is lower than the existing block distribution of sewer line, all newly designed sewage is pumped with the closed ABS "PIRANHAMAT" 1001D system or similar/equivalent. All atmospheric sewage is piped through the manhole into a future connection to the street network.

Fecal sewage

The plot is equipped with utility.

The existing connection to the street sewerage network is satisfactory, it is not necessary to reconstruct it. Newly designed fecal sewage collects vertically and runs into the basement floor. As the distribution level  is lower than the existing block sewer distribution, all newly designed sewage is pumped with a closed ABS "PIRANHAMAT" 1001W or similar/equivalent.

Reinforced concrete manhole 01000 with cover D400 is installed on the existing block distribution of sewage.

All sanitary blocks are provided with gullies with stainless steel grille and breath valves according to the HL system

Water supply

Consumable water

The plot is equipped with utility.

The existing connection to the street water supply network does not satisfy newly designed consumers. It is planned to reconstruct the existing water meter manhole and to install newly designed water meters. The reconstruction of the existing connection to the street network and the installation of water meters is the sole responsibility of the PUC.  Planned connection is 0100 mm.

Installation of water meter oB0 for hydrant network is planned in the water meter manhole, installation of water meter for consumption water 032, the existing water meter is retained for the existing objects on the plot.

The supply of consumer water is directly from the city network. The pressure in the city network is satisfying.

The pipes in the ground are laid over the bottom covered with sand, after the installation has been tested for water permeability and the record has been made, with the presence of the Supervisory Authority, the pipes are filled with sand above the pipe 10 cm in the trench width. Sand should be moisten, ie. wetted and then covered with excavated soil in compacted soil until it is fully compacted with possible wetting.

Hydrant Network

The hydrant network supply requirement is 10 l / sec.

The water supply to the hydrant network is resolved from the city network 10 l / sec.

The available pressure in the city network does not satisfy consumers. A pressure booster system is located in the ground floor room. The room is equipped with gully and fire doors. Hydraulic Calculation is enclosed in the design documentation and envisages simultaneous operation of two external hydrants or one external and two internal 10 I / sec.

Pumps are provided PPHU 3D 1+1Q=600-10001/min. P1=3 kw P2=3,0kw or equivalent.

Beside each external hydrant there is a cabinet for hoses and tools for activating the hydrant for the immediate fire extinguish. The cabinet is pasted onto lightweight reinforced concrete base. External hydrants are designed on a distance greater than 5 meters from designed building avoid a demolition zone in case of fire, also external hydrants are less than 80.0 m apart, which satisfies the fire regulations from the aspect of external hydrant network. Certified documentation is required for all incorporated materials from authorized institutions.

Testing the pressure on the hydrant network and the amount of water it provides is carried out by an authorized organization that is authorized for this type of test and issues a certificate confirming the functionality of the hydrant network performed as proof that the installation is correct and can be put into operation.

The internal hydrant cabinets are planned in accessible and visible places easily visible, in the communication parts of the building, the internal hydrant network is planned from galvanized steel pipes.

The internal hydrant cabinets are metal fitted with a ball valve, nozzle and synthetic hose L = 15.0 m. The cabinets are marked with a huge red H letter.

2. TECHNICAL DESCRIPTION ARHITECTURE

Introduction

The building under construction was designed in Zrenjanin and is located on plot number 7540 CM Zrenjanin I, in Dr Kornel Radulovic Street. The plot has an area of 913 m2. The building is within the scope of the PGR "Southeast" plan in Zrenjanin (Official Gazette of the City of Zrenjanin No. 32/14). The building is designed as a business, number of floors -1, B1 + GF + 1F. The site in question houses the family residential building No.1 and the auxiliary building No.2 which have been destroyed and self-ruined and must be removed. Parts of the foundation of the building will be reconstructed. According to the General Regulation Plan "Southeast", the purpose of the whole building will change from residential to business.

Building 1- family residential building, on the plot, number of floors GF, BRGP = 123 m2

Facility 2- auxiliary building, on the plot, number of floors GF, BRGP = 52 m2

Building 3-auxiliary building, on the plot, number of floors GF, BRGP = 119 m2

Building 4- auxiliary building, on the plot, number of floors GF, BRGP = 79 m2

Program structure and architecture of the building

The building is, by its purpose, a business building , by type it is building  in a broken row, with a plot width of 12.48m. The overall height of the building, in the highest part, is 11.77m (92.42 m).

The facility envisages 6 offices with an average area of about 16 m2, located in the basement and on the remaining 2 floors, with accompanying spaces for communication, archives, toilets and kitchenettes.

Levelling of access-entry, vertical and horizontal communication in the building

The connection to the public road is maintained from Dr. Kornel Radulovic Street via plot number 9648. Parking space is provided in front of the plot with four parking spaces, while two parking spaces are provided on the plot in question. Parking spaces in front of the lot will be constructed from pd raster cubes, and parking lot frames will be made of specially shaped raster in order to notice the separation of individual parking lots for passenger vehicles.

The building is functionally zoned so that the technical rooms are located in the basement. There is one entrance to the facility as well as one vertical communication (staircase). The approach and entrance to the building, as well as the flows of horizontal and vertical communications around and within the building, are clearly defined and levelled in importance.

The staircase vertical is at the base of the building so as to ensure smooth communication and easy movement through parts of the building. In the basement are designed: entrance halls, staircase vertical, technical rooms with an exhibition area where the used technologies are perceived, the accompanying office and the toilet. On the high ground floor there is a projected office space, with an archive, toilets and a kitchenette. There are offices, a meeting room, a toilet and a kitchenette on the first floor.

OBJECT MATERIALIZATION

Building construction

Constructive assembly: the object is solved as two independent skeletal structures of the same number of floors.

Bearing structure of the part of the building where the offices are is made up of AB solid slab resting on the AB columns. The construction of the entrance part of the building consists of steel columns and beams.

The inter floor structures is made of AB solid slabs.

The construction of the building foundation is arranged as two independent-dilated AB slabs. The AB foundation walls are formed in two orthogonal directions below the ground pillars, where they extend to the level of the elevation of the terrain. The roof structure on the part of the building where the offices are located is filled with a solid AB slabs above the last floor, over which sheet metal cover with adequate hydro and thermal insulation is laid, and on which there are photovoltaic panels. The roof structure of the entrance part of the building is solved like a glass roof with steel beams. The slopes of the roof planes are 23% and 30%, respectively (4 separate roof planes).

Building facades

The materialization and treatment of the façade is in accordance with the design task, with the tendency to satisfy the aesthetic and functional values of the building. The exterior walls are partly designed as a sandwich wall with facade brick, while the entrance and basement have glass panels.

Interior finishing

The interior walls are made of brick d = 12 cm. Finishing the interior walls is plastering and painting with distemper. In the kitchens, the walls are covered with ceramic tiles from the floor up to 150 cm in height, and in the toilets from the floor to the ceiling. The floors in the kitchens, bathrooms, staircases, in the auxiliary rooms in the basement, as well as in the hallways are made of ceramic tiles, and in the office spaces the floors are made of parquet

Joinery

The facade joinery is aluminium, glazed with triple insulation glass. The interior joinery in the auxiliary and sanitary rooms is made of wood and MDF, painted with polyurethane varnish, while the doors of the offices are made of aluminium profiles, glazed with double glass.

INSTALLATIONS

The installation of the facility provides:

-electrical installations

-water supply and sewerage

- heating and cooling installations

- IT installations.

Electrical installations

Power supply to the facility is planned through the existing measuring group, meter no. 10637669 (ED number 361 77861).

The intended maximum simultaneous (engaged) power of consumers in the newly designed facility is 24.56kW, and therefore it is necessary to provide a connection 3x400 / 230V, with limiters of rated current 42A.

Power supply to the facility will be provided in accordance with the conditions of the competent ODS.

There are 3 separate cabinets of automation in the whole facility, each on each floor: RO-Su, RO Pr, RO-Sp which are used for regulation at the whole facility level, ie: control of substation, ventilation, lighting, shutters, while other automation equipment located in the field is used for controlling FC units and for local lighting and shutter controls.

The automation cabinet in the RO-Su basement should consist of a central control unit, executive IQ modules and associated electrical equipment (power supply of modules, relays, terminals, cables). In addition to all equipment, control equipment for lighting and ventilation in  toilets is also provided.

Ground floor and floor automation cabinets RO-Pr and RO-Sp are designed to contain lighting, shutters and ventilation control equipment in toilets and kitchens.

All cabinets are connected by communication (HDL network) cable JH (St) H 2x2x0.8 mm2 or similar characteristics, thus enabling coupling of all elements of automation into a single system.

Inside the automation cabinet is an energy section that powers local plug sockets and consumers that are not part of the Smart Buildings system.

PP-y 5 x 6 mm2 cables have been designed to power the distribution boxes of automation on the floors of the building (RO-Su, Ro-Pr and RO-Sp).Touch overvoltage protection is provided by the automatic power cut-off system of the TT system.

The protection of cables and installation wires against short circuits and overloads is provided with appropriate fuses, located at the beginning of the power outlet and sized in accordance with the cross-section, type and method of laying the cables, and in accordance with SRPS HD 60364-5-52.

The lightning rod installation of this facility will be in the form of a classic lightning rod, as a non-insulated lightning rod installation according to SRPS IEC 1024-1. The required level of lightning protection is determined on the basis of SRPS IEC 1024-1-1. By calculating the lightning rod installation, taking into account all the relevant factors, it was found that a protection level of 111 was required, with a average distance between the leads of less than 20m and a width of the receiving mesh less than 10m.

The galvanized steel strip FeZn 25x4 mm, laid at the foundation of the building below the waterproofing, shall be used as a electrode. The strip will run from the foundation grounding electrode to the ground level between the hydro insulation and soil. The galvanized steel strip FeZn 25x4 mm laid through the columns will be used as the down conductor when concreting the columns (up to the test joints). Above the test joints (below the façade or through concrete columns) and to the roof, a down conductor of aluminium Al 010 is laid.

The lighting arresters will be the Al 010 aluminium reception conductors with support at 1m distances. Test joints are installed at the main down conductors at a height of 1.50m from the ground.

The bottom of the gutter verticals (the gutters are used as auxiliary drains), the rail for equalization of potentials and other metal parts on the facade or the roof of the object larger than 2m2 are connected to the lightning rod installation.

Water supply and sewage

The connection to the existing water supply network is planned for the object. The required amount of hot water is 1l / s and 10l / s of water for the needs of the fire hydrant network. The planned connection to the city water supply network is 100mm, in accordance with the conditions of the competent authority.

Connection of dimensions 160mm is provided for sewage network

Heating and cooling installations

Vitocal 300-G type BW or similar/equivalent heat pumps are planned for the heating of the newly designed building.

Indoor installations consist of heaters and pipe work. Three-pipe parapet fan coil units are provided as heaters. Fan coil units operate in heating mode in winter and in cooling mode in summer. The ventilation of the premises is provided naturally.

IT installations

Connection to optical infrastructure or 2 telephone lines and one ADSL port are planned

4. TECHNICAL DESCRIPTION STRUCTURE

Foundation conditions

A geomechanical study for the parcel in question was not made. The soil is assumed to consist of building detritus  and humus of alluvial  sand dust, alluvial sand with rare dust layers, yellow color and deeper gray sand up to a depth of 15m, which belong to the second soil category on which the foundation  construction can be made and manual and mechanical  excavation could  be carried out.. The foundation structure below the multi-storeyed part of the building is reinforced concrete slab of regular shape as well as strip foundations along the perimeter of the building and under the walls. The contact load based on previous experience is 100kN / m2, the foundation depth is in the zone of delluvial sediments. Groundwater is assumed registered at a level of 2m from the surface. The structure consists of the following structural elements:

- Foundation slab under basement 30cm thick

The bottom contour of the foundation slab is parallel to the tip of the foundation slab . The foundation structure was calculated as a slab on an elastic substrate with a coefficient of bedding K = l0000 kN / m3

Foundation slab

The foundation slab of the multi-storeyed part of the building is of the correct geometry, placed over the poured stone material, insulation and bedding. Funding at -1.3 lm. The thickness of the slab is It was designed as a foundation counter slab  with a reactive load from the ground below the building in the amount of 100 kN / m2, on which, from above, the main supporting columns, concrete basement walls were designed, while between the walls were designed columns that extend to higher floors. Staircase to the ground floor is also relayed on teh foundation slab. Ribbed reinforcement B500B is provided. The anchors dropped from the foundation slab depend on the diameter of the reinforcement adopted, and it is adopted to allow the anchors to overtake the contour of the 50-diameter reinforcement slab used. The foundation slab is connected to the foundation beams, which are located in the main vertical axes of the object, with a rectangular geometry, 40 cm wide and 60 cm high. The foundation structure of the entrance hall is a 30cm thick foundation slab, which is dilated from the foundation of the main building. They are loaded with a reactive load from the ground. Columns and vertical walls are supported on the foundation structure. The reinforcement of the base structure is meshed with the addition of ribbed in the zone of greatest impact.

Ground floor

The ground floor reinforced concrete slab is designed on one level, without any deleveling. Slab thickness is 20cm. Slab ranges vary from 650cm to 665cm  is relied on reinforced concrete frame beams. The slabs are loaded with standard types of workloads, floor layers, walls and useful loads for office space. There is an opening for the stairs measuring 127cm x 483cm.

First floor slab

The intermediate floor at +5.30 is 20cm thick. According to the courtyard, it is left 328cm in relation to the main pillar, while on other facades there is no culvert. The slab is supported by columns and beams. The opening in the slab is for the staircase and measures 127cm x 420cm. They are loaded with layers of construction, walls and useful loads. Maximum range is 665cm.

Roof slab

Three reinforced concrete roof slabs of 18cm thickness were designed. The bottom of the slab is at an elevation of 8.34m and the top of the slab is at an elevation of 11.27m. The slopes of the panels are 26 ° and 23 °. A static slab system  is a slab that supports in both directions, resting on the frame beams.

Reinforcing

All slabs are reinforced with a combination of ribbed and mesh reinforcement. The mesh reinforcement forms a basic grid at 15 cm and additional ribbed reinforcement bars are placed over it, according to the calculation. The ends of the overhanging plate are reinforced by the positions in Cyrillic letters П, while the additional main reinforcement in both directions is crossed above the supports. In the areas where theslab is most stressed by shear stresses due to puncture, reinforcements are designed in the form of reinforcement pieces that form frames around the columns.

BEAMS

The basic bearing structure of the objects is reinforced concrete frames that are placed in orthogonal directions in the main axes of the objects. There are two frames on the façade, while there are 4 frames in the transverse direction. Frames in the transverse direction are 152cm + 223cm + 2293cm (center distance). Large structure overhang is accepted by reinforced concrete beams 30cm x 50cm in center axles and 25cm x 50cm in end axles. The roof structure is formed by beams of rectangular cross section 25x50cm, 25x70cm.

Reinforcing

The beams are reinforced with main ribbed reinforcement and smooth reinforcement for stirrups. The main armature diameters are 14-18mm, while the stirrups are 8mm in diameter. The stirrups are designed as torsion bars with overlapping over the smaller beam dimension.

MAIN COLUMNS

Basement

Basement columns are divided by position on the basis of extensive and internal. The associated surface of the concrete ceilings and the loads carried by these columns influence the dimensions of the cross-section of the column. Columns measuring 25cm x 30m have been adopted, as well as vertical ring beams 25cm x 25cm. Inner columns are 30cmx40cm and 40cmx50cm. The columns are freestanding. A new column continues on each of these columns on the next floor. MB30 concrete quality. Ribbed reinforcement 14mm in diameter, ribbed stirrups 8mm, overlapping for torsion impacts over shorter dimensions.

Ground floor

The main columns on the ground floor panel differ from the lower level. There is a cross-section reduction, according to the plan of positions. MB40 concrete quality. Ribbed reinforcement 16mm in diameter, ribbed stirrups 8mm, overlapping for torsion impacts over a shorter dimension.

First floor

Above the slab of the first floor, the columns continue according to the plan of positions. MB30 concrete quality. Ribbed reinforcement 14mm in diameter, ribbed stirrups 8mm, overlapping for torsion impacts over shorter dimensions. The dimensions of the columns are 25cm x 40cm.

Reinforcing

The reinforcement used for the pillars is ribbed B500B, for main feed bars and smooth GA 340/360 for stirrups. The reinforcement diameters are 14mm while the stirrups are 8mm in diameter, folding over one side of the column (torsion stirrups). The reinforcement of the column is hanged over the plate 50 of the adopted bar, which represent the anchors for the next floors.

CONCRETE WALLS

Basement

Reinforced concrete walls at the lowest level are designed reinforced concrete walls 25cm thick, 150cm high are placed on the outline of the foundation slab, through the lowest floor. They are also stuck in the foundation slab.

Reinforcing

All reinforced concrete walls as well as stairways are reinforced with MA 500/560 mesh reinforcement in both zones along the middle of the wall. At the ends of the wall and at the points of intersection of the walls reinforcing cages are formed from the ribbed reinforcement B500B and transverse for the stirrups.

STAIRS

For the vertical transportation of the users of the building, stairs are provided according to the graphic documentation. On each floor there is a projected single-flight staircase with dimensions of 127 cm in width and 15 cm thick sloping boards.

Entrance hall construction

The entrance hall structure is designed as a steel structure consisting of cross-sections that support the glass facade. The dimensions of the hall are basically 580cm x 387cm. Steel profiles [] 100xl00x4 have been designed for vertical and horizontal elements to which a glass-field facade is mounted on an aluminium profile structure. Hall height is variable. The lowest construction is 920 cm high, while the highest part is 1235 cm high. The facades are completely glass except in the lowest part where the glass is placed in two of the 3 facade surfaces. The roof structure is made of steel profiles that rely on the basic steel structure. The slope of the roof deck level is 30 °. The roof cover is a glass surface on a structure made of aluminium profiles.

THE CHOICE OF MATERIALS FOR LOADBEARING STRUCTION

Quality of construction material:

- MB 30 concrete - for horizontal supporting elements (beams, slabs)

- MB 40 concrete - for vertical supporting elements (columns, walls, stairs)

- reinforcement GA 240/360 - for stirrups of columns, beams and rc shear walls

- BS00b reinforcement - as main reinforcement of columns, beams and rc shear walls, as additional reinforcement

Reinforcement for concrete slabs:

- MA 500/560 - as the main reinforcement for concrete

- slabs for main supporting entrance hall construction - steel class c0361 (S235 - eurocode)

- Brick wall block

- Solid brick for partition walls

- Gravel as a bedding underneath the foundation slab

5. TECHNICAL DESCRIPTION  POWER INSTALLATIONS

General data

The building is designed as a business, number of floors Po + VP + 1. The following rooms are located in the basement:

- office

- show room

- two toilets

- storage room

- entrance hall with staircase

- On the high ground floor are the following premises:

- three offices

- two toilets

- archive

- hall with staircase

- kitchenette

- storage room

- Upstairs are the following premises:

- two offices

- meeting room

- two toilets

- hallway with staircase

- kitchenette

- storage room

Classification of external impacts

The application of the standard SRPS HD 60364-5-51 covers the selection of equipment and its installation. It provides common rules for compliance with security measures, requirements for proper functioning against the intended use of installations, and requirements corresponding to the intended external influences.

The selection of equipment according to external influences is necessary not only for proper functioning, but also to ensure the reliability of security measures in accordance with the rules of SRPS HD 60364 in principle. The protection measures achieved by the construction of the equipment are only valid under the given external influence conditions, provided that appropriate testing of the equipment specification has been carried out under these external influence conditions.

Classification of External Impact

AA4 Ambient Temperature -5 ° C to + 40 ° C

AC1 - Altitude: S 2000m

AD2- presence of water - droplets in free fall

AE1 - presence of foreign solids - negligible

AF1 - presence of corrosive or dirt - negligible

AG1 - mechanical stress, impacts - weak

AH1 - mechanical stress, vibration - weak

AK1 - presence of the flora or fungus - negligible

AL1 - presence of the fauna - negligible

AM1 - electromagnetic, electrostatic or ionization effects - negligible

AN1 - solar radiation – negligible

AP1 - seismic effects - negligible

AQ1 - lightning - negligible

Usage classification

BA1 -staff competence - uninformed

BB1 - electrical resistance of the human body - normal

BC1 - touch of staff with earth potential - no touch

BD1 - presence of small number people, good evacuation capability

BE1 - nature of material being processed or stored - no danger

Classification of building construction

CA1 - Material composition - Non-flammable

CB1 - Building structure – Negligible

Power supply and measurement of electricity consumption

The power supply of the facility is provided in accordance with the Terms for design and connection specified by EPS DISTRIBUTION LLC Belgrade, Branch of the Electricity Distribution Zrenjanin No. 8B.1.1.0.-D-07.13.-96111-19 19 March 25, 2019 in which is defined as follows.

- Voltage to which the object is connected: 0,4kV

- Maximum power: 42kW

- Power factor: above 0.95

- Indirect Touch Voltage Protection System: TT system

- Connector Type: Special Purpose

- Connector character: permanent

- Connection points of the object: measuring cabinet, behind the measuring device

- Connection points: The closest pole of the LV network at dr. Kornela Radulovica Street, in front of number 18.

- Description of connection to the measuring point: existing connecting line

- Measurement site description: existing measuring location cabinet

- Measurement device: Exsisting meter, meter number: 10637669, ED number: 36177861

- Control device: within the measuring device

- Protective Devices: Existing

- Electricity delivery point: measuring cabinet, behind the measuring device

- Maximum short-circuit current allowed: 6kA

- The power supply to the facility will be provided by the PP00 4 x 25mm2 and PP0O 2 x 1.5 mm2 cable laid from OMM to GRO in the wall of the building.

- PP-y 5 X 6 mm2 cables have been designed to power switchboards across the floors of the building (RO-Po, Ro-Pr and RO-Sp)

Distribution cabinets

For the supply of energy, an existing measuring cabinet (OMM) is used, which is built into the wall in front of the building, such that it is accessible to persons for control and reading. The OMM cabinet is equipped with a measuring device, power limiter - 63A Type C rated current limiters, 10kA cut-off power, and connection terminals.

The connection is 3x400 / 230V, the maximum one-time (engaged) power consumption of the object is 28kW.

Measuring device - meter, is three-phase, three-system, two-tariff.

The accuracy class of active energy meters is 2, that is, class A, in the range 10 - 80 A.

The main distribution cabinet (GRO) is equipped with  FID fault interrupt circuit 63 / 0.5A, as well as with rated current 25A, type C 10kA fuse, for protection of conductors for the power of the distribution cabinets of floors, as well as equipment for external illumination in accordance with the provide single-pole scheme.

Each of the floor cabinets (RO-Su, RO-Pr and RO-Sp) is equipped with a FID fault interrupt circuit 25 / 0.3A, appropriate elements for controlling lighting, ventilation, heating, shutters, or elements of the smart home system, as well as adequate fuses for  protections power lines of all consumers.

In distribution cabinets, automatic circuit breakers are Bi C characteristics with rated currents in the range of 10-20A, breaking power 10kA, depending on the consumer type.

Distributions cabinets are made of double-decapitated sheet metal in appropriate IP protection (IP31 or larger). The cabinets are intended for in wall mounting.

The cabinets are equipped with single pole scheme mounted on the inside of the cabinet door.

On visible place of cabinet, on the outside, the protection system is marked : TT

Installation of electrical connections and sockets

Electrical connections are provided with PP-y cables of the appropriate cross-section and the number of wires. Laying of cables is carried out in the wall under the plaster.

Modular connection boxes in the wall are provided for powering of part of the consumers in the building, and depending on need they can be with 1, 4 or 7 modules.

Modular sockets are a combination of Shuko sockets, Euro sockets, RJ45, or for the purpose of the room in which they are installed. In addition to wall sockets, floor boxes with a certain number of power and RJ 45 connectors are also provided for certain rooms, in accordance with the graphic documentation.

For kitchen areas and rooms for machine equipment, sockets with a protective cover are provided.

The distribution boxes for the installation are mounted axially at a distance of 30 cm from the non-plastered ceiling, taking into account the depth of in-built.

The cable routing between the distribution (078 mm) and terminal (060, M4 and M7) boxes is at right angles to the axis of the box.

In the toilets, distribution boxes are not provided and are installed on the outside of the wall. There may be only one power cable in the distribution box.

The electric lighting installation is performed with appropriate luminaries adapted to the working conditions and interior decoration. When selecting the lighting, LED lighting was selected to maximize energy savings.

The lighting is designed with LED recessed or surface luminaries of adequate power.

Control of lighting is described below in the design description of smart building installation. The installation is maintained at a height of 30 cm from the ceiling while the distribution boxes 078 mm are mounted axially at the intersection of verticals and horizontals at a height of 30 cm from the ceiling.

The luminaries are intended for mounting on ceiling, wall or structure construction in a manner conditioned by the construction of the luminaries or by means of specified mounting accessories. Position of luminaries in Bill of quantities also includes a structure for hanging luminaries, which is fixed on the spot. A brief description is provided for each projected luminaries. Luminaries supply voltage is 220-240V, 50Hz. The composition of the luminaries contains light sources, and all the auxiliary material for the luminaries’ operation and installation (holders, hangers, cables). All luminaries in offer should be from the same reputable manufacturer. All offered luminaries should have the same or similar characteristics and dimensions as the above types of luminaries. If the type of luminaries changes, comparing with the offer, it is necessary to submit complete technical documentation on the basis of which it can be determined that the offered luminaries corresponds to the design. The luminaries manufacturer shall operate in accordance with the ISO 9001: 2008 quality management system, the ISO 14001: 2004 environmental protection management system and the OHSAS 18001: 2007 occupational health and safety management system or equivalent.

Conductors

The entire installation was performed with PP-Y conductors, with the appropriate cross-section and the number of wires laid in the wall and underneath the plaster or under the building floor. All conductors are protected by appropriate fuses depending on the power of the consumers.Structural cabling system (SKS) installations are provided with cables type S / FTP Cat.6

Installations for equipotential bounding

Connect all metal parts throughout the building with a PP-Y-1x6 mm2 conductor. Conductor is installed in the wall -under the plaster and is connected to the installation of plumbing, heating and other metal masses in the building. Only the junction point between the conductor and the metal pipe is carried out by special clamps, and the flat metal masses are connected with a conductor with the help of lugs and screws. The connection itself must be made as close as possible to the outlet of the plumbing pipe from the wall.

Conductor P/Y 1x6 mm2 will be positioned from the connection point to the equipotential bounding box or  to the closest distribution cabinet. All these conductors are connected to the fifth rail in the switchboards.

Earthing and lighting installation

The lightning rod installation of this facility will be in the form of a classic lightning rod, as a non-insulated lightning rod installation according to SRPS IEC 1024-1. The required level of lightning protection is determined on the basis of SRPS IEC 1024-1-1. By calculating the lightning rod installation, taking into account all the relevant factors, it was found that a protection level of 111 was required, with a average distance between the leads of less than 20m and a width of the receiving mesh   less than 10m.

The galvanized steel strip FeZn 25x4 mm, laid at the foundation of the building below the waterproofing, shall be used as a electrode. The strip will run from the foundation grounding electrode to the ground level between the hydro insulation and soil. The galvanized steel strip FeZn 25x4 mm laid through the columns will be used as the down conductor when concreting the columns (up to the test joints). Above the test joints (below the facade or through concrete columns) and to the roof, a down conductor of aluminium Al 010 is laid.

The lighting arresters will be the Al 010 aluminium reception conductors with support at 1m distances. Test joints are installed at the main down conductors at a height of 1.50m from the ground.

The bottom of the gutter verticals (the gutters are used as auxiliary drains), the rail for equalization of potentials and other metal parts on the facade or the roof of the object larger than 2m2 are connected to the lightning rod installation.

Interior lighting installation

With interior lighting installation ensure equipotential bonding prevent potential induced voltages and surge of atmospheric originated over-voltage in the interior of the building. Equipotential bonding will be performed inside the building with the bus for main equipotential bonding. Connect the main bus for equipotential bonding to the earthing system, lightning rod installation, plumbing and heating installation.

Protection against high   touch voltage

Protection against high touch voltage is provided by the automatic shutdown of the power supply to the TT system. The protection of cables and installation wires, against  short circuits and overloads, is provided with appropriate fuses, mounted at the beginning of the power outlet and dimensioned according to the cross-section, type and manner of cable laying, and in accordance with SRPS HD 60364-5- 52.

The protection against direct contact of parts under the voltage has been implemented in accordance with the applicable legislation, ie the corresponding IP protection.

Protection against indirect contact with parts under the voltage has been carried out in accordance with the applicable legislation, ie switching off the protective device within the prescribed time.

All metal parts of the equipment that are not normally under voltage are galvanically connected and grounded. This results in equipotential bounding on all metal parts, which is a protection against static electricity and atmospheric discharge.

The protection against penetration of solid foreign objects and moisture is carried out by placing the equipment in the housing of the appropriate IP protection. The protective conductor, the third or fifth wire in each cable, is yellow-green in color. The complete installation must be carried out in accordance with the applicable Technical Regulations.

DESCRIPTION OF THE CENTRAL SYSTEM OF CONTROL AND MONITORING - SMART BUILDING

Description of automatics distribution cabinets

There are 3 separate cabinets of automation in the whole facility, each on each floor: RO-Su, RO Pr, RO-Sp which are used for regulation at the whole facility level, ie: control of substation, ventilation, lighting, shutters, while other automation equipment located in the field is used for controlling FC units and for local lighting and shutter controls.

The automation cabinet in the RO-Su basement should consist of a central control unit, executive IQ modules and associated electrical equipment (power supply of modules, relays, terminals, cables). In addition to all equipment, control equipment for lighting and ventilation in toilets is also provided.

Ground floor and floor automation cabinets RO-Pr and RO-Sp are designed to contain lighting, shutters and ventilation control equipment in toilets and kitchens.

All cabinets are connected by communication (HDL network) cable JH (St) H 2x2x0.8 mm2 or similar characteristics, thus enabling coupling of all elements of automation into a single system.

Inside the automation cabinet is an energy section that powers local plug sockets and consumers that are not part of the Smart Buildings system.

Description of elements in the automation field

In addition to the cabinets, there is also automation equipment that is arranged in space - in rooms or with elements of machine installations. These include: temperature sensors (space, in tubes), pressure and humidity sensors, certain elements such as valve drivers and control equipment (touch screens, FC unit controllers, buttons). These last elements are used for zoning, that is, for controlling devices by zones.

Touch screens have access to the entire system by which they connect via wireless provided they are connected to the same network. Touch screens, controllers and buttons allow local control of devices and temperatures in zones. They are located in individual (defined) zones such as offices, and through them it is possible to control lighting, shutters, heating and cooling of any zone: in other words, each touch screen allows control of any zone, not just the one in which it is physically located. The program of each touch screen is divided into several screens that are accessed through a simple and intuitive graphical interface. All programs are identical and the home screen can be adapted to the room in which it is located. For example, the home screen in office 1 the home screen should be just office 1.

All buttons are connected centrally to the digital inputs of the corresponding automatic control cabinet. Each button is programmed separately and its function is not predefined for the room it is located in.

Subsystem for   lighting control in the building

This subsystem is intended for lighting management both inside and outside. The inclusion of a specific lighting group on the premises should be realized via the button or touch screen that prompts the demand for connection on controller. This means that the lighting is not directly controlled in such a way that the switch interrupts the circuit, but this function is realized by pressing a button to request the controller to switch on or off a certain group of luminaries.

Controlled lighting can be on / off type or dimmable; depending on this, the appropriate module similar to- HDL-MR0410.431 (module for control of 4 on / off lighting circuits, maximum current 10A) or similar to HDL MDT0203.433 (module for dimming 2 circuits for maximum current 3A) should be used. In the halls and toilets, PIR sensors are provided that are programmed to send a request to the controller to switch on certain lighting when detecting movements.

Subsystem for control of roller shutters in the building

Similar to the lighting controlling subsystem, shutters are controlled in the facility: via a touch screen or via buttons located in specific room sit is possible to raise / lower the shutters. Pressing the button a request to the controller that drives the shutter motor directly is sent. Identically to manual control of shutters it is possible to partially or fully raise / lower the blinds, as well as to activate automatic control (positioning of shutters depending on time of day, etc.). The modules used to control the shutters are similar to HDL-MW02.431 (2-shutter motor control module). Automatic control of the lighting subsystem and roller shutter is intended for use through predefined scenarios, ie. operation summary: in addition to individual, manual operation, different scenarios (raise / lower all shutters, opening hours, holidays, ...) will be available on touch screens, allowing one sequence of buttons to trigger a sequence of commands for which Manual execution would otherwise require a considerable amount of time and visit of each room.

Monitoring and control subsystem for heating

Local Control of the FC unit should be realized through the use of wall-mounted touch screen controllers ( similar to SE8300) in offices on all floors and in the halls. With these controllers it is possible to manually control the desired temperature and signal the presence in the room after working hours, thus enabling the continuation of the heating or cooling operation. The controllers are designed for wall mounting at a height of 150cm from the finished floor, above the controls for lighting and shutters for accurate measurement of temperature. In the graphics documentation, the controllers are marked by rooms (eg SE8300_16, where 16 is the number of room in which the wall controller of the FC unit is located) Control of the heating and cooling operation is enabled by the use of a relay accessory (similar to SC3504), and at least one relay accessory is assigned to each controller. As much as one zone has FC units, so much should be provided for the relay accessories that will be run from one SE8300 controller or equivalent. Control of heating or cooling is performed by analogous control of the valve operation on the FC unit itself, as well as by selecting one ad 3 speed of the FC unit. The relay accessories are mounted directly on the FC unit, and are powered by local power cabinets, ie automation. In order to ensure efficient heating / cooling and achieve greater efficiency, it is necessary to provide the installation of magnetic contacts on the windows. In this way, their connection with the appropriate controller will ensure that the operation depends on the open / closed window. The number of magnets is predicted by the Bill of quantities and arrangement of the equipment in the field so that one magnet is mounted on each window pane so that their exact number depends on the final number and arrangement of the windows in the building. In case there is more than one magnet (window) in one zone, the zone controller connects to the first one in a row, while all others are connected by a regular connection. In this way, the opening of any window signals to the controller a change of status in the zone. The controller of the FC unit similar to SE8300 has an integrated presence sensor, and it will be possible to reduce the heating / cooling to the required level or switch it off completely when all users leave the office. This should also enable large savings to be generated. If the room is large, external PIR sensors should be provided which will provide the controller with additional information about one's presence in the room. For the equipment elements in the field no special cable distribution lines are foreseen, more precisely laying of the cables for connection between the sensor and the controller will be defined on the spot, during construction. All zone controllers are integrated into a single system that allows zone management through a central computer or tablet, as well as the ability to send offset temperatures from them. The goal of this realization is to achieve as much controllability as possible.

The Smart Buildings system solution should allow heating / cooling in the building for multiple modes, e.g. regular working hours, weekends, holidays, etc. During regular days it is necessary to enable working time configuration. During working hours, the heating is regulated via wall controllers, while out of business hours the Smart Building should realize that individual zones are heated / cooled only at the request of the user in order to optimize energy consumption.

Substation controlling subsystem

The substation consists of an energy efficient heat pump that works on water / water principle, a pair of circulation pumps and three-way valves that, depending on the operating module, push the water to one side or the other. The coupling between the heat pump and the Smart Building system is provided via a communication card which should be delivered with the heat pump and it will ensure the connection of heat pump. The card connects directly with the RO-Po cabinet to the central unit of automation. Communication cards are specified in the design of thermo technical installations and must be delivered with a heat pump.

Microprocessor substations

The microprocessor substation is located in the cabinet for automatics in the basement. In addition to the microprocessor substations, the automation cabinets are equipped with all the necessary protection and control equipment (switches, relays, signal lamps) for proper operation. The following equipment is provided in this automation cabinet:

The command voltage source is also distributed: 230 / 24VAC voltage transformer, protection switches, command voltage switches, auxiliary relays, etc. and programmable controllers along with the central processing unit.

Schneider Electric programmable logic controller - StruxureWare (SXW) microprocessor station or similar/equivalent performs the following functions independently and autonomously:

- direct digital control (DDC) programme logic control (PLC) time programs

- functions of the trend

- historical data bank energy optimization

- exchange of information with other substations

- own control of hardware and software and alarm generation in case of failure

The central unit used in this project is Automation Server. The aforementioned modular controllers are connected by power, communication and input-output (1/0) modules, which are mounted on a DIN rail to power and carry the module. The 1/0 module is powered by an internal communication protocol, and the power supply is provided by Power Supply, which is powered by 24Vac. The maximum number of corresponding 1/0 modules that can be connected to one Power Supply is limited to 30W, and the Automation Server limitation is communication with 32 1/0 modules.1/0 modules are adapted to the various requirements for receiving and processing signals from field equipment and are grouped by function into:

signalling and counting modules (potential-free permanent and pulse contacts)

measuring and positioning modules (inputs: LG-Ni 1000, pt1000, Ni1000, 0-10VDC, 4-20mA, outputs: 0-10VDC, 4-20mA)

on / off modules (permanent and pulse controls, voltages up to 250V)

control modules (0-10V or 4-20 mA)

The following modules  or similar are to be used in this project:

- UI   SXWUl16XX10001 Module with 16 analog / digital inputs

- DO   SXWDOA12X10001Module with 12 digital (relay) outputs

- AO  SXWAOV8XX10001 Module with 8 analog outputs

All 1/0 modules are designed for mounting in automatic cabinets.

In addition to the non-listed microprocessor substations of modularnig type, the project also envisages systematic Bae Net MSTP IP controllers or similar/equivalent that integrate fan coil control across floors. These system controllers serve to integrate room controllers of the SE8300 type (maximum of 64 SE controllers per line) or similar to the projected central Smart Building central system. Namely, the control of fan-coil units in the facility is done through local SE controllers, so that one controller manages up to 8 fan coil units. This solution allows you to control the fan speed, choice of summer / winter regime, formation of groups of several fan coils that belongs  to the same  technological whole.

Delivery of  SE controllers and the services of their installation, connection, programming and commissioning as well as installation for powering the controllers, connection of fan coil units, controllers and other equipment in the field are not the subject of this design, but are covered by electrical installation design. This design envisages only the installation (BACnet bus cables or similar) of the equipment (MSTP controllers) and the BMS level services necessary to connect the SE8300 controller or similar to the smart building design system.

Software

Software integrates lighting controlling systems, FC units and shutters into a single software solution. The interface and features should be similar to Magiesta software which have been developed for all computers, tablets and smart phones. It is envisaged that the software will be installed on the central computer which will be located at the reception desk. In addition, it is planned to be installed on tablets that will be located in the conference rooms and allow local control and launch of a predefined scenario.

Management and control of lighting, FC and shutter operation is done through a graphically oriented interface consisting of connected windows, with each space representing one logical unit (eg one conference room). Software should allow easy view of the current status of all devices connected to this software.

Structural cable system installations - sks

The project envisages the integration of the telephone and computer systems through a single system (structured cabling system). The installation of the structural cable system is provided in accordance with ISO / IEC 11801 and EN 50173 standards as well as the recommendations of leading equipment manufacturers in the field. The system enables data transmission within different computer network architectures (Fast / Giga Ethernet, ATM, etc.), transmission of speech, sound and video signals. The system enables reliable transmission of different types of signals at frequencies up to 500 MHz (Cat. 6).

The computer and telecommunications network is designed to support the following services:

- standard internet services (web access, e-mail service, remote access, wi fi access, file sharing, etc.),

- other services based on TCP / IP protocol.

The main concentration of the structural cabling system (SKS) is a built-in 19 "rack cabinet, measuring 600x450x900mm (SxDxV). The front door is made of glass, fitted with a lock and key, while the sides and back can be easily removed for mounting the equipment. The cabinet is fitted with standard equipment: fan panel, patch panels, cable trimmers, power strips, channels for vertical cable leading, cabinet marking and grounding equipment. Cabinet is located in room 0-9-archive, on the ground floor.

The power supply to the cabinet is provided from the closest existing distribution cabinet of electrical installations.

Telecommunication sockets in the space are provided according to the requirements of the investor.

The cable installation is provided with halogen-free sheaths of S / FTP type 4x2xAWG23 Cat6a, which allows the transmission of different types of signals at frequencies up to 500 MHz. The cables are laid through halogen free ribbed tubes in the wall / suspended ceiling.

The entire installation must be designed in accordance with the applicable technical regulations for this type of installation. After completion of all work, measurements and testing of all electrical installations, visual inspection and functional testing should be carried out in accordance with regulations, rules and other legal normative governing this area. All measurements and tests should be carried out by accredited institutions and reported to the investor. All installed materials and equipment must be provided with appropriate attestation documentation in accordance with national legislation.

Measurements, tests and attest documents

After completion of all work, measurements and testing of all electrical installations, visual inspection and functional testing should be carried out in accordance with regulations, rules and other legal normative governing this area. All measurements and tests should be carried out by accredited institutions and reported to the investor. All installed materials and equipment must be provided with appropriate attestation documentation in accordance with national legislation.

6. TECHNICAL DESCRIPTION MECHANICAL INSTALLATION

Interior installations

Indoor installations consist of heaters and pipework. Three-pipe parapet fan coil units are provided as heaters. Dispositions of heating elements and piping are shown in the graphic documentation. Fan coil units operate in heating mode in winter and in cooling mode in summer. Hot air condensation occurs during the summer, due to its cooling; the condensate is discharged through the condensate network to the boiler room and from there to the sewer.

Boiler room

The boiler room is located in the basement of the building.

Main components are similar equivalent to:

- Vitocal 300-G, type BW

- Vitotronic 200, type WOlCP DHW cylinder

- Water heater inter-boiler

- NC box (Natural cooling set)

- External heat generator with Vitotronic 200

- Solar installation for heating of consumable water Medubiler of water for heating

Room heating with heat pump

If the temperature of the inter boiler is lower than the set value set on the control of the heat pump, then the heat pump and the secondary pump are activated.

Heat pump 1 supplies the heating circuit with heat. The flow temperature of the heating water, and therefore the heating circuits, is regulated by the control of the heat pump 2. The secondary pump 6 transports the heating water to the water boiler inter-boiler. The heat pump, primary pump and secondary pump are switched off when reached setpoint on the integrated return temperature sensor.

The pumps of heating circuits transport the necessary quantities of water to the heating circuits.

In order to equalize the difference in the amount of energy between the primary and secondary circuits, a heating water inter-boiler is provided in parallel with the heating circuits. The heat that is not taken up by the heating circuits is accumulated in the heating water inter-boiler. In addition, this results in a long operating time of the heat pump 1. In the event of blockage by the power distributor, the inter-boiler heating water supplies the heating circuits with heat.

Heating the consumed water with a heat pump

In the delivery state, the heating of the consumable water by means of heat pump 1 is set as a priority over the heating circuit.

The heating request is realized via the upper temperature sensor of the storage tank and the control of the heat pump 2. The control of the heat pump 2 controls the circulation pump for heating the storage tank. The heat pump 1 raises the temperature of the supply line to the value necessary to heat the consumable water. With the help of an external heat source, the temperature of the storage tank can increase to over 65 ° C.

Heating the consumed water with a solar support

The control of the heat pump 2 can be connected via KM-BUS distributor to the Vitosolic 100, type SD1 or similar, in order to be able to heat the consumed water with solar support. If the temperature difference between the collector temperature sensor and the storage tank temperature sensor exceeds the set point, the circulation pump is switched on and the DHW storage tank is heated. The DHW cylinder is heated through the solar installation performs over set point in Vitosolic 100, type SD1 31 or similar/equivalent.

“Natural cooling” function

In combination with NC box, the heat pump 2 controls the cooling of the building. If the outside temperature or room temperature exceeds the cooling temperature limit that can be set at the control of the heat pump 2, then the cooling function "natural cooling" is unblocked by the control of the heat pump 2. Circulation pumps in NC box are switched on, and the 3-way switch valve switches to cooling.

Through the under floor heating circuit, heat is discharged from the room, and via the plate heat exchanger in the NC box is transferred to the primary circuit. The primary circuit transfers heat to the ground. In parallel with the cooling mode, the hot water pump 1 can heat the consumable water

7. TECHNICAL DESCRIPTION HYDROTECHNICAL INSTALLATIONS

The existing connection to the street water supply network does not satisfy newly designed consumers. It is planned to reconstruct the existing water meter manhole and to install newly designed water meters. The reconstruction of the existing connection to the street network and the installation of water meters is the sole responsibility of the PUC.  Planned connection is 0100 mm.

Installation of water meter oB0 for hydrant network is planned in the water meter manhole, installation of water meter for consumption water 032, the existing water meter is retained for the existing objects on the plot.

The supply of consumer water is directly from the city network. The pressure in the city network is satisfying. Calculation is done and attached to the design.

The pipes in the ground are laid over the bottom covered with sand, after the installation has been tested for water permeability and the record has been made, with the presence of the Supervisory Authority, the pipes are filled with sand above the pipe 10 cm in the trench width. Sand should be moisten, ie. wetted and then covered with excavated soil in compacted soil until it is fully compacted with possible wetting.

Sewage

Fecal sewage

The plot is equipped with utility.

The existing connection to the street sewerage network is satisfactory, it is not necessary to reconstruct it. Newly designed fecal sewage collects vertically and runs into the basement floor. As the distribution level  is lower than the existing block sewer distribution, all newly designed sewage is pumped with a closed ABS "PIRANHAMAT" 1001W or equivalent.

Reinforced concrete manhole Fi 1000 with cover D400 is installed on the existing block distribution of sewage.

All sanitary blocks are provided with gullies with stainless steel grille and breath valves according to the HL system

Atmospheric water

Atmospheric water is drawn from the roof into vertical gullies through a sink with a heater and a basket, yard traps with cast iron frames and grilles and everything is collected into a lifting device.