## Priced bill of quantities
Design and Construction Supervision Joint Stock Company, I 17 Kralja Petra Boulevard, 21000 Novi Sad, Commercial Account 340-1376-70, TIN SR 101637004, Telephone: 021/477-0096; 444-819, Fax: 021/444-819, Laboratory: 021/6432-821; web site: www.vojvodinaprojekt.rs; е-mail: office@vojvodinaprojekt.rs
NOT TO BE FILED
INFORMATIVE BILL OF QUANTITIES
FOR THE REPAIR OF THE HYDRO TECHNICAL COMPLEX OF KLEK
* The exact amounts of the material used and the scope of work shall be established by direct on-site measurement and calculated in the measurement book. * Dimensions of all elements to be checked on-site.
VOJVODINAPROJEKT

## 1.1.Arh.work on techn. building
pos. | Description of works | UoM | Quantity | cena € | Unit price in RSD | iznos € | Total price in RSD
ARCHITECTURAL WORKS ON TECHNICAL BUILDING
1 | DISASSEMBLY AND DEMOLITION
Prices of positions shall include all cleaning, loading and unloading of debris and removed material to the truck, as well as all vertical and horizontal transport on the construction site and removal of debris to the municipal landfill at distance up to 15 km.
Before conducting the dismantling arrange the manner and the place of disposal of the dismantled elements, furniture with the Investor, as well as the manner and place of removal and handover to the Investor, which should be fully included in the price of the position.
The price of the position shall include, also, the closing of plumbing, various sealings of pipes, power circuit shutdown etc.
1.1. | Removing furniture
Removal of existent furniture elements from the ground floor and transport to the place determined by the Investor, at distance up to 15km.
| Calculation per m2 of floor surface | m2 | 120 | 1
1.2. | Dismantling of tiled stove
The dismantling of the tiled stove, dimensions 2.5x2x10, cleaning of elements and removal to a dry place with the preparation for reinstallation.
On the occasion of demolishing, conduct the recording of internal channels and provide the installation scheme for the purpose of reinstalling.
| Costs shall be charged per piece | pcs. | 1 | 100
1.3. | Removal of flat single lap roof tiles
Tiles should be removed carefully and taken to a landfill up to 15 km away. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m² | m2 | 250 | 2.45
1.4. | Removal of ridges and bumps
The ridges and bumps must be removed from roof safely. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m | m | 18.8 | 2.45
1.5. | Removal of roof battens
The battens shall be removed carefully, loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m² | m2 | 250 | 2.45
1.6. | Partial removal of rafters
Damaged rafters (up to 40%) should be carefully removed, cleaned and stacked for reinstallation or loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km.
| Costs shall be charged per m² | m2 | 100 | 2.45
1.7. | Removal of roof flashing
The usable material should be collected, loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
Costs shall be charged per
| a. Roof flashing | m2 | 65.08 | 4.8
| b. Roof frontal boards | m | 30 | 1.5
1.8. | Removal of loft floor
The removal should be done carefully, with the usable material being cleaned, loaded onto a truck and transported to a landfill designated by the Investor at a distance up to 15 km. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m² | m2 | 122 | 6.4
1.9. | Removal of chimneys, above the roof
Mark and carefully disassemble chimney parts, clean them and transport them to the construction landfill. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill. The price shall include auxiliary scaffolding too.
| Costs shall be charged per piece. | pcs. | 2 | 70
1.10. | Removal of downspouts, window flashings, chimneys and other elements
The metal sheets shall be removed, packed, loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km.
Costs shall be charged per
| a. Per m | m | 51.2 | 1.8
| b. Per m2 | m2 | 4 | 2.6
1.11. | Removal of wood flooring, beds and sand layer, together with skirtings
The wood flooring, sub-floor, beds and skirtings should be removed, loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m2 | m2 | 38.23 | 4.6
1.12. | Removal of vinyl floor
The vinyl should be removed, packed, loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km.
| Costs shall be charged per m2 | m2 | 74.88 | 2.8
1.13. | Removal of base under floors, thickness up to 10 cm
Remove the base, load it onto a truck and transport it to a landfill designated by the Investor at a distance of up to 15 km.
| Costs shall be charged per m2 | m2 | 68.23 | 4.2
1.14. | Removal of the concrete floor slab
The debris should be collected, taken out, loaded onto a truck and transported to a municipal landfill up to 15 km away.
Costs shall be charged per m2
| b. Thickness up to 12 cm. | m2 | 74.88 | 9.8
| d. Per m³. | m3 | 0.5 | 74
1.15. | Demolition of panels of the wooden floor structure on both sides
The usable material should be cleaned, loaded onto a truck and transported to a landfill designated by the Investor up to 15 km away. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m2 | m2 | 121.88 | 12
1.16. | Removal of the stairway fence made of old format bricks
Remove the stairway fence carefully. The price shall include auxiliary scaffolding too. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m3 | m3 | 5.83 | 30
1.17. | Demolition of concrete and stone stairs
The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m | m | 22.4 | 3.85
1.18. | Demolition of yard brick fence, built in flexible mortar
Bricks should be cleaned from mortar and stacked for rebuilding. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m3 | m3 | 2.4 | 34
1.19. | Demolition of concrete sidewalk
Sidewalk demolition should include the removal of sidewalk base. The hard materials should be separated and transported to a landfill designated by the Investor at a distance of up to 15 km. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m2 | m2 | 52.76 | 9.5
1.20. | Removal of brick facade walls in flexible mortar
The usable bricks should be cleaned from mortar and stacked at the construction waste dumpsite. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill. The price shall include auxiliary scaffolding too. The demolition amount shall be determined by the Contractor and Supervisor on-site.
| Costs shall be charged per m3 | m3 | 1 | 50
1.21. | Careful removal and transport of windows
The removed windows should be assembled, loaded onto a truck and transported to a landfill designated by the Investor.
Costs shall be charged per piece.
| a. Up to 2 m². | pcs. | 1 | 8
| b. Between 2 and 5 m². | pcs. | 7 | 16
1.22. | Removal and transport of exterior doors
The removed doors should be assembled, loaded onto a truck and transported to a landfill designated by the Investor.
Costs shall be charged per piece.
| b. Between 2 and 5 m². | pcs. | 3 | 14.95
1.23. | Removal of paint from doors and windows by using heat gun
The existing layers of paint should be removed by using heat gun, as well as scrapers and other suitable tools. The procedure should be repeated until all paint layers are removed and clean wood is reached. Pay special attention not to damage the edges and profile details. After removing the paint, the wood is treated with fine sandpaper.
| Costs shall be charged per m2 | m2 | 73.8 | 4.8
1.24. | Removal of window bars to be reinstalled
Mark the bars and remove them carefully, taking care not to damage them. Clean the bars and leave them at a covered construction waste dumpsite.
| Costs shall be charged per piece. | pcs. | 3 | 14.5
1.25. | Careful disassembly of ceramic tile flooring set in cement mortar
Remove the tiles and substrate to the concrete structure. Remove mortar from tiles and stack them. The debris shall be taken out, loaded onto a truck and transported to a municipal landfill.
Costs shall be charged per m2
| a. From ceramic tiles | m2 | 6.08 | 14.95
1.26. | Disassembly of wooden stairs
The wooden stairs should be removed carefully, loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m2 | m2 | 3 | 6.6
1.27. | Partial stripping of mortar off interior walls
The Supervisor and the Contractor shall determine, in writing, surfaces to be stripped off mortar. Strip the mortar off and clean the joints with cramp irons up to the depth of 2 cm. The brick surfaces shall be cleaned with steel wire brushes and wall shall be washed with water. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill. The quantity includes the surfaces plastered with breathable mortar.
Costs shall be charged per m2
| b. Flexible mortar | m2 | 710 | 2.9
1.28. | Striping mortar off facade walls
After stripping mortar off, use cramp irons to clean the joints up to the depth of 2 cm and clean the surface of facade wall bricks with steel wire brushes and wash with water. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
Costs shall be charged per m2
| b. Flexible mortar | m2 | 161 | 4.75
1.29. | Careful stripping of mortar from vaults and arches
Mortar stripping should be done carefully, taking care not to damage the brick surface. After stripping mortar off, use cramp irons to clean the joints up to the depth of 2 cm, and clean the surfaces of vaults and arches with steel wire brushes and wash with water. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m2 | m2 | 19.1 | 3.8
1.30. | Stripping wall ceramic tiles and mortar
Strip tiles with mortar off, use cramp irons to clean the joints up to the depth of 2 cm, and clean the surface bricks with steel wire brushes. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m2 | m2 | 15 | 3.8
1.31. | Stripping mortar off the ceiling with the ceiling structure of cane and battens
Mortar should be stripped off, the debris collected, taken out, loaded onto a truck and transported to a municipal landfill at a distance of up to 15 km.
| Costs shall be charged per m2 | m2 | 131.07 | 2.7
1.32. | Removal of sanitary ware
Sanitary fittings and valves should be dismantled and transported to a landfill at a distance of up to 15 km, as chosen by the Investor.
Costs shall be charged per piece
| faucet (single handle) | pcs. | 1 | 5
| squatting water closet with toilet cistern | pcs. | 1 | 35
| washbasin | pcs. | 1 | 7
1.33. | Careful removal of metal doors and window bars
The removed doors should be assembled and handed over or loaded onto a truck and transported to a landfill designated by the Investor, at a distance of up to 15 km.
Costs shall be charged per piece
| a. Doors | pcs. | 1 | 12
| b. Window bars | pcs. | 1 | 9
1.34. | Removal of metal fence and gate
Fence should be carefully removed, its parts roughly cleaned and stacked at the warehouse for reuse or loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
Costs shall be charged per m2
| b. Metal fences | m2 | 6 | 2
| b. Metal gates | m2 | 8 | 3
1.35. | Removal of the water supply network, consisting of steel galvanised pipes
Water supply network should be dismantled, while unusable material should be loaded and transported to a landfill at a distance of up to 15 km, as chosen by the Investor. Facility of up to 100 m² in size
| Costs shall be charged on a lump sum basis | Lump sum | 1 | 75
1.36. | Dismantling of sewers
Sewers should be dismantled, while unusable material should be loaded and transported to a landfill at a distance of up to 15 km, as chosen by the Investor. Facility of up to 100 m² in size
Costs shall be charged on a lump sum basis
| b. Cast iron pipes | Lump sum | 1 | 55
1.37. | Removal of lights
Remove all lights, both those installed on the wall and on the ceiling carefully. Remove to a place designated by the Investor.
| Costs shall be charged per piece | pcs. | 16 | 4
| TOTAL DISASSEMBLY AND DEMOLITION |  |  |  |  | 0
2 | PREPARATION AND EARTHWORKS
2.1. | Manual excavation of Class 3 soil for stairway
Manual soil excavation for stairway up to the depth of 80 cm. Cut the edges carefully. Level the excavation bottom. Earth is set aside, at least 2.0 m from the edge of the construction pit.
| Costs shall be charged per m3 | m3 | 3 | 9.5
2.2. | Manual excavation of Class 3 soil for pavements
Manual soil excavation for sideways up to the depth of 20 cm. Cut the edges carefully. Level the excavation bottom. Earth is set aside, at least 2.0 m from the edge of the construction pit.
| Costs shall be charged per m3 | m3 | 10.55 | 9.5
2.3. | Removal of excess soil from ground floor premises
Removal of excess soil from ground floor premises, loading onto a truck and transport to a landfill at a distance of up to 15km
| Costs shall be charged per m3 | m3 | 24 | 12
2.4. | Manual excavation of soil in premises with temporary disposal at side
The excavated soil should be backfilled with compacting without wetting.
Costs shall be charged per m3
| Trench within the facility | m3 | 25 | 9.5
| Trench on the external side of the facility | m3 | 25 | 8.5
2.5. | Transport of excess soil from the excavation
Transport of excess soil from the excavation to a landfill at a distance of up to 15km. The precise location of the landfill shall be specified by the Supervisor and the Investor.
| Calculation per m3 of original soil, transported and dispersed at the landfill. | m3 | 13.55 | 5.5
2.6. | Procurement, transport, dispersal in layers, compacting and fine planning of gravel
Filling gravel base under strip foundations, floor slab and sidewalks, free of organic and other impurities. Compacting with adequate compacting tools with 10cm thick layer.
| Costs shall be charged per m3 | m3 | 38 | 22.5
TOTAL PREPARATION AND EARTHWORKS
3 | CONCRETE WORKS
3.1. | Laying reinforced concrete foundations in soil MB 20
Concreting of reinforced concrete stairway strip foundation footings, t=80cm, with MB20 concrete. Price should include all works on preparation and concreting. After concreting, concrete maintenance should be provided.
| Costs shall be charged per m3 of the completely built and processed concrete. | m3 | 2.5 | 110
3.2. | Construction of the reinforced concrete floor slab MB 20
Concreting reinforced concrete floor slab thickness t=10cm, with MB20 concrete. The price shall include all preparatory works, concrete works and installation of Q-138 (10x10cmm ...4.2mm) wire-mesh reinforcement in the lower slab area. After concreting, the concrete maintenance should be provided.
| Costs shall be charged per m2 of the completely built and processed concrete. | m2 | 125 | 12
3.3. | Construction of smooth reinforced concrete walls MB 20
Concreting reinforced concrete stairway walls t=13cm, with MB20 concrete. Form smooth wall formwork and reinforce with mesh reinforcement. Concrete should be built in and maintained in accordance with regulations. Costs shall include the formwork, supports, reinforcement and auxiliary scaffolding.
| Costs shall be charged per m3 | m3 | 2.5 | 135
3.4. | Construction of concrete sidewalk, thickness 10 cm, of MB 20 type
Concreting sidewalk, thickness t=10cm, with MB20 concrete. The cost shall include all preparation and concreting works, as well as the required formwork. The upper surface should be trowelled. Concrete in 2m sections with pressed joints. After concreting, the concrete maintenance should be provided.
| Costs shall be charged per m2 of the completely built and processed concrete. | m2 | 55 | 120
3.5. | Building stairs of the basement stairway with MB 20 concrete
The concreting and installation of stairs at the at the place of existing stairs, with MB20 concrete. The cost shall include all preparation and concreting works, as well as the required formwork. The upper surface should be trowelled. After concreting the stairs, the concrete maintenance should be provided.
| Costs shall be charged per m | m | 10.5 | 25
| TOTAL CONCRETE WORKS |  |  |  |  | 0
4 | MASONRY WORKS
4.1. | Building waterproofing protection
Building the inner side of the skirting wall with shiner out in the flexible mortar 1:2:6, as waterproofing protection.
| Costs shall be charged per m2 | m3 | 23 | 10
4.2. | Construction of the damaged parts of facade with solid first class bricks, thickness 12 cm, in flexible mortar, ratio1:1:6
Whole bricks and halves of straight cut edges should be used for building the lining of the reinforced concrete stairway. The joints should be formed by using squared or circular iron rod, with a cross section matching the thickness of joints. Layout pattern must be regular. While conducting masonry works, mortar leaking should be prevented. The joints should be treated with cement mortar, ratio 1:2. Grouting is included in the cost. The connection with the construction walls shall be conducted with anchors, 5 pieces per m².
| Costs shall be charged per m2 | m2 | 7 | 34
4.3. | Building of the damaged parts of facade with solid bricks, with stretcher out, with 25 cm thickness, first class in the flexible mortar, ratio 1:1:6
Whole bricks are used for final caps of the reinforced concrete stairway wall. The joints should be formed by using squared or circular iron rod, with a cross section matching the thickness of joints. Layout pattern must be regular. While conducting masonry works, mortar leaking should be prevented. The joints should be treated with cement mortar, ratio 1:2, according to designer’s instructions. Grouting is included in the cost.
| Costs shall be charged per m | m2 | 12 | 16.5
4.4. | Construction of walls, t=25 cm and more, by solid bricks in flexible mortar, 1:2:6
The bricks should be wetted before laying. Walls should be built in regular layout pattern. Joints should be cleaned up to the depth of 2 cm. The price shall include auxiliary scaffolding too. The actual quantity shall be determined by the Contractor in agreement with the Supervisor, after stripping the mortar off the walls.
Costs shall be charged per m3
| Solid brick | m3 | 1 | 110
| Solid brick of old format | m3 | 1 | 125
4.5. | Plastering of brick walls by applying flexible mortar in two layers.
Before plastering, the wall surfaces should be cleaned and sprayed with milk. The first layer should be built with flexible mortar of sieved gravel type “One”. The substrate should be wetted, the first mortar layer should be applied and roughened. The second layer should be prepared with fine and clean sand, without mud and organic substances and applied over the first layer. Plaster with wetting and flattening with small trowels. The plastered surfaces must be flat without breaks and waves, while edges have to be sharp and straight. The mortar should be wetted in order to avoid quick drying and “burnout”. The price shall include auxiliary scaffolding too.
Costs shall be charged per m2
| Old format bricks | m2 | 610 | 8.3
| Over rabitz mesh | m2 | 20 | 9.2
4.6. | Plastering of walls, substrates for glueing of tiles with flexible mortar.
Before plastering, the wall surfaces should be cleaned well and sprayed with cement milk. Apply a layer of mortar with sieved gravel, of “One” type, and smooth it. The plastered surfaces must be flat and rough. The price shall include auxiliary scaffolding too.
Costs shall be charged per m2
| Old format bricks | m2 | 10 | 6.5
4.7. | Plastering of walls by applying flexible mortar in two layers
The flexible mortar should be made with sieved gravel, “One”, the first layer of mortar should be applied and roughed. The second layer should be prepared with fine and clean sand, without mud and organic substances and applied over the first layer. Plaster with wetting and flattening with small trowels. The plastered surfaces must be flat without breaks and waves, while edges have to be sharp and straight. The mortar should be wetted in order to avoid quick drying and “burnout”. The price shall include auxiliary scaffolding too.
| Costs shall be charged per m2 | m2 | 48.6 | 8.3
4.8. | Plastering of vaults by applying flexible mortar in two layers..
The flexible mortar should be made with sieved gravel, “One”, the first layer of mortar should be applied and roughed. The second layer should be prepared with fine and clean sand, without mud and organic substances and applied over the first layer. Plaster with wetting and flattening with small trowels. The plastered surfaces must be flat without breaks and waves, while edges have to be sharp and straight. The mortar should be wetted in order to avoid quick drying and “burnout”. The price shall include auxiliary scaffolding too.
| Costs shall be charged per m2 | m2 | 67.8 | 14.5
4.9. | Plastering of facade walls by applying flexible mortar in two layers.
Before plastering, the wall surfaces should be cleaned and sprayed with milk. The first layer should be built with flexible mortar of sieved gravel type “One”. The substrate should be wetted, the first mortar layer should be applied and roughened. The second layer should be prepared with fine and clean sand, without mud and organic substances and applied over the first layer. Plaster with wetting and flattening with small trowels. The plastered surfaces must be flat without breaks and waves, while edges have to be sharp and straight. The mortar should be wetted in order to avoid quick drying and “burnout”. The price shall include auxiliary scaffolding too. Before plastering, all elements on the facade built with solid bricks should be protected from dirt and damage.
| Costs shall be charged per m2 | m2 | 192.8 | 10.5
4.10. | Plastering of brick walls with repair breathable mortar.
Plastering should be performed with repair breathable mortar of SikaMur Dry or other similar type, according to the manufacturer’s instructions. The quantity includes surfaces above the horizontal waterproofing at 80 cm height.
| Costs shall be charged per m2 | m2 | 130 | 10.5
4.11. | Building cement screed
Building of cement screed min. 6cm thick, reinforced with Schultz mesh, with overlaps or fibres. The upper surface should be treated so that it is suitable for placing of ceramic tiles. Before laying the screed, the screed substrate should be cleaned and washed. The screed mortar should be prepared with sieved gravel type “One”, ratio 1:3 and maintained it until it hardens.
| Costs shall be charged per m2 | m2 | 125 | 12
4.12. | Building of chimney above the roof
Use whole bricks to build the chimney and its cap. The joints should be formed by using squared or circular iron rod, with a cross section matching the thickness of joints. Layout pattern must be regular. While conducting masonry works, mortar leaking should be prevented. The joints should be treated with cement mortar, ratio 1:2, according to designer’s instructions. Grouting is included in the cost. The chimney and the chimney cap should be done fully in line with the existent chimney.
| Costs shall be charged per m | m | 2 | 65
4.13. | Building of tiled stove
Building of tiled stove dim. 2.5x2x10 with the existing materials with the addition of 20% of new elements, fireclay bricks and other consumable materials
| Costs shall be charged per sets | pcs. | 1 | 600
| TOTAL MASONRY WORKS |  |  |  |  | 0
5 | REINFORCING STEEL WORKS
5.1. | Rebars installation
Procurement, cutting, bending and installation of rebars. Price includes all necessary works and materials.
Calculation per kg of installed rebars.
| MA 500/560 | kg | 400 | 1.1
| B500B (RA 400/500) | kg | 80 | 1.1
| TOTAL REINFORCING STEEL WORKS |  |  |  |  | 0
6 | INSULATION WORKS
6.1. | Horizontal waterproofing of walls
Drill the horizontal holes Ø12mm in horizontal joints at the maximum axis distance of 12cm. The holes should be 2-3cm shorter than the wall thickness. The drilled holes should be cleaned of dust with compressed air. Inject the silane-based Sikamur-InjectoCream or other similar emulsion. Prepare according to the manufacturer’s instructions.
Costs shall be charged per m.
| a. Thickness up to 30 cm. | m | 9 | 23
| b. Thickness up to 50 cm. | m | 4.2 | 31
| c. Thickness up to 65 cm. | m | 64 | 37
6.2. | Vertical waterproofing of external walls
Vertical waterproofing of the rime walls on inner side with waterproofing glass wool strips with 4mm thickness, with adequate coatings and welded overlaps of 10 cm at least. The welded 10 cm overlaps also pertain to the connection with the horizontal waterproofing of walls and floors.
| Calculation per m2 of effective surface | m2 | 23 | 15
6.3. | Waterproofing basement brick walls (Bauplus or Texas penetrant)
Joints should be filled and tuck-pointed. The dried and cleaned wall would be wetted with water and wiped horizontally with a brush under the penetrant paste. To be repeated with two more coatings, vertically and horizontally. The previously applied coat must be dry, whereby drying lasts 12-24 h, but no longer than 24 h. Make sure the premise is clean, without dust and that the walls don’t have unstable parts, as well as grease stains. Before applying the penetrant, form grooves at the connection of walls and between walls and floors, dimensions 2cmx2cm. Fill grooves with a thicker penetrating compound. The price shall include auxiliary scaffolding too.
| Costs shall be charged per m2 | m2 | 48.6 | 27.5
6.4. | Waterproofing the basement brick walls (with Bauplus or Texas penetrant)
Joints should be filled and tuck-pointed. The dried and cleaned wall would be wetted with water and wiped horizontally with a brush under the penetrant paste. To be repeated with two more coatings, vertically and horizontally. The previously applied coat must be dry, whereby drying lasts 12-24 h, but no longer than 24 h. Make sure the premise is clean, without dust and that the walls don’t have unstable parts, as well as grease stains. Before applying the penetrant, form grooves at the connection of walls and between walls and floors, dimensions 2cmx2cm. Fill grooves with a thicker penetrating compound. The price shall include auxiliary scaffolding too.
| Costs shall be charged per m2 | m2 | 67.8 | 30.5
6.5. | Waterproofing the basement concrete floors and stairways (with Bauplus or Texas penetrant)
The dried and cleaned floor would be wetted with water and wiped with a brush under the penetrant paste in one direction. Repeat the procedure with yet two coatings, perpendicularly to the preceding one. The previously applied coat must be dry, whereby drying lasts 12-24 h, but no longer than 24 h. Make sure the premise is clean, without dust and that the floors don’t have unstable parts, as well as grease stains. Any possible uneven surfaces are to be filled with a thicker penetrating compound.
| Costs shall be charged per m2 | m2 | 53.27 | 27.5
6.6. | Construction of thermal insulation of the flooring of the ground floor
Construction of thermal insulation of the flooring of the ground floor using EPS insulation boards in a 10cm thick layer installed over waterproofing. ESP insulation boards are to be covered with a protective PVC film. For the purpose of concreting floor layers, install 1cm thick XPS insulation boards at the points of contact with the wall (floating floor).
| Calculation per m2 of floor surface | m2 | 125 | 8
6.7. | Construction of thermal insulation between ceiling joists
Procurement and installation of thermal insulation made of mineral wool, in a 20cm thick layer, between ceiling joists. A vapour barrier is to be installed on the lower side and a waterproof vapour permeable film on the upper side, with both elements included in the price.
| Calculation per m2 of floor surface | m2 | 135 | 20
| INSULATION WORKS, TOTAL |  |  |  |  | 0
7 | CARPENTRY
7.1. | Replacement of worn out and damaged elements of the roof structure
Procurement of materials, manufacturing and replacement of worn out and damaged elements of the roof structure. New elements should be made from dry softwood lumber modelled on the disassembled elements, dressed and installed with all required connections. The price shall also include struts and fasteners.
New purlin elements should be used to construct an eave on the gable wall, 90 cm
| Costs shall be charged per m3 | m3 | 6 | 410
7.2. | Procurement and installation of sheathing over the roof structure
24 cm thick planks made of dry, straight and high-quality fir planks of optimum length are to be installed close together and riveted up.
| Costs shall be charged per m2 | m2 | 185 | 8
7.3. | Procurement and installation of dressed sheathing over the roof structure as an eave flashing
24 cm thick planks made of dry, straight and high-quality dressed fir planks of optimum length are to be installed on contact and riveted up (eave flashing over the rafters on the upper side).
| Costs shall be charged per m2 | m2 | 65.08 | 10
7.4. | Procurement and installation of waterproof vapour permeable film over the sheathing
Install the film and paste the joints using a self-adhesive reinforcement acrylic strip.
| Costs shall be charged per m2 | m2 | 250 | 2.4
7.5. | Roof lathing with 48/48mm battens, parallel with the rafters, over the sheathing, for the purpose of forming air space under the cover
Install battens over the rafters. Lath the roof using dry, straight and high-quality fir battens, of optimum length.
| Costs shall be charged per m2 | m2 | 250 | 2.8
7.6. | Roof lathing with 28/48 mm battens, orthogonally to the rafters, over longitudinal battens, for the purpose of covering with interlocking tiles
Install battens over longitudinal battens. Lath the roof using dry, straight and high-quality fir battens, of optimum length.
| Costs shall be charged per m2 | m2 | 250 | 3.4
7.7. | Procurement, installation and disassembly of the form for concreting of staircase walls
The form is to be made as a double form of 24mm thick fir planks and strips of appropriate cross section, according to the precisely specified measures, and it is to be coated with old oil or similar. It is to be disassembled carefully, without shocks.
| Costs shall be charged per m2 | m2 | 8 | 12.4
7.8. | Procurement and installation of a dressed fascia board of the rafters
24 cm thick planks made of dry, straight and high-quality dressed knot-free fir planks of optimum length are to be installed on contact and riveted up (flashing of the face side of the rafters).
| Costs shall be charged per m | m | 30 | 3.8
7.9. | Protective coating of wooden roof elements
Wooden elements of the roof structure, ceiling, joists, eave flashing and other are to be protected from insects, algae, fungi and decay with two to three coatings, using a chemical agent as chosen by the Designer.
| Costs shall be charged per m2 | m2 | 250 | 3.5
| CARPENTRY, TOTAL |  |  |  |  | 0
8 | PLASTERING
8.1. | Partition walls made of gypsum cardboard panels
Construction of a partition wall made of 12.5mm thick gypsum cardboard panels, with 10cm total wall thickness. The structure consists of 75mm thick UW and CW galvanized sections. The filling is mineral wool. The empty space is used to set water, drainage and electrical installations. Panel joints are to be bandaged and treated with a skimming compound. All works are to be performed in line with the manufacturer’s instructions.
| Costs shall be charged per m2 | m2 | 26 | 20
8.2. | Reinforced door frame
Manufacturing of a reinforced door frame in a gypsum cardboard wall, 10cm thick, made of 2mm thick galvanized sections.
| Item 3 clear span 71/225 | pcs. | 1 | 45
8.3. | Ceiling made of monolithic gypsum cardboard panels
Construction of the ceiling made of 12.5mm thick double gypsum cardboard panels over the stud frame consisting of cross-installed CD/UD sections. Sections are to be fixed directly to the joists. In the sanitary block, moisture-resistant boards are to be used.
| Costs shall be charged per m2 | m2 | 122 | 18
8.4. | Suspended ceiling 60x60cm
Construction of a dismantling suspended ceiling in a 60x60cm grid made of mineral fibre boards with a metal stud frame hung to the ceiling at the points of wooden joists. The ceiling suspension is 15-25cm high. Lights are to be installed in the grids.
| Costs shall be charged per m2 | m2 | 122 | 20
8.5. | Gypsum cardboard masks
Construction of drainage pipe masks in the ceiling made of 12.5mm thick moisture-resistant boards by screwing them to the metal stud frame made of galvanized steel sections. Panel joints are to be bandaged and treated with a skimming compound.
| Costs shall be charged per m2 of constructed surface | m2 | 12 | 14
| PLASTERING, TOTAL |  |  |  |  | 0
9 | TILING WORKS
9.1. | Laying of ceramic floor tiles
Procurement of materials and glueing of granite slip-resistant wood-look ceramic floor tiles, 1st class, 60x20cm, by applying adhesive. Tiles are to be glued along the length of the room broken by 1/2, with zero joints. The price shall also include waste.
| Costs shall be charged per m2 | m2 | 72 | 32
Plinth of the same material, 10cm high
| Costs shall be charged per m1 | m1 | 40 | 15
9.2. | Tiling of stairs and landings with ceramic tiles
Tiling is to be conducted using 1st class tiles, by applying adhesive, as chosen by the Designer. Prepare the base in advance. Grind the tile edges manually, if needed. Tiled surfaces must be flat. Grout the joints and clean laid tiles. The price shall also include tile procurement.
Costs shall be charged per
| a. Staircases and landings | m2 | 12.18 | 34
| b. Staircase skirting | m | 12.5 | 14
9.3. | Installation of 20x30 cm ceramic wall tiles by applying adhesive
Procurement of materials and gluing of 60x30cm ceramic wall tiles, 1st class, by applying adhesive onto plastered walls and walls made of gypsum cardboard panels. They are to be laid horizontally by butting them together without joints. The tiles are to be in two shades at the most. The price shall also include installation of aluminium angle strips. In sanitary blocks, wall tiles are to be laid 2.10m high (in 7 lines).
The quantity shall include sanitary blocks and kitchen work area up to the height of 150cm.
| Costs shall be charged per m2 | m2 | 63 | 24
| TILING WORKS, TOTAL |  |  |  |  | 0
11 | JOINERY WORKS
11.1. | Manufacturing and installation of wide box double glazed windows with interior shutters
Windows and shutters are to be made from 1st class dry fir or spruce timber, according to the joinery plan and details and in all aspects in line with the existing windows and shutters, provided that both casements open inward. The windows should be fitted with stays to secure the casements when they are open. Exterior casements are to be glazed with thermal insulating glass Ug≤1.30W/m2K and the interior ones with 4 mm thick clear float glass and sealed with the appropriate putty. The cross section of casements is to be adjusted to the glass weight. Seal window frames and casements with EPDM caulk sealant. Construct shutters with movable slats and opening at an 180 degree angle. Prior to their installations, windows and shutters are to be protected with a colourless impregnation coating. They are to be installed recessed by 1/2 a brick from the facade.
Costs shall be charged per piece
| Item 1 dim. 1.11x1.80 | pcs. | 7 | 950
| Item 2 dim. 1.11x0.68 | pcs. | 1 | 340
11.2. | Manufacturing and installation of entrance doors with a fanlight
Doors, doorframe and threshold are to be made of first class, dry oak wood, according to the joinery plan and details, in all aspects in line with the existing doors. Install door finish hardware, cylinder lock and three keys, three mortise hinges per leaf, as chosen by the Designer. Doors are to be protected with a colourless impregnation coating. A rubber bumper is to be installed on the floor. Fanlight should be glazed with thermal insulating glass Ug≤1.30W/m2K.
Costs shall be charged per piece
| Item 3 dim. 1.29x2.25+0.84 | pcs. | 2 | 650
| Item 4’ dim. 1.15x2.39 (basement) | pcs. | 1 | 520
11.3. | Joinery repair of interior doors
Replace damaged parts of doors and door frames by 40%. Replace all door handles and locks for the purpose of uniformity.
| Costs shall be charged per piece | pcs. | 9 | 160
11.4. | Manufacturing and installation of single-leaf solid doors
The doors are to be without threshold, outfitted with standard door finish hardware and Elzett locks. Installation into the 10cm thick gypsum cardboard panel wall.
Costs shall be charged per piece
| Item 7 prod. measures 71/210 | pcs. | 1 | 200
11.5. | Manufacturing and installation of a glazed interior partition
Outfit the partition with venetian blinds on the side of the office
Costs shall be charged per piece
| Item 8 prod. measures 90/90 | pcs. | 1 | 120
11.6. | Painting of old windows and doors whose old paint has been stripped off
Type of paint, producer and colour are to be chosen by the Designer. Before painting, the wood is to be sanded, cleaned and coated with an acrylic primer with added oil-based paint. Apply the first coat of putty and coat with oil-based putty, sand the surface and apply the second coat of putty. Paint with an oil-based paint, when dry, sand the surface and apply another coat of oil-based putty. Fine sand and paint using enamel paint.
| Costs shall be charged per m2 | m2 | 122.8 | 8.4
11.7. | Painting of new windows and doors with semi-transparent finishes, including varnishing
Type of paint, producer and colour are to be chosen by the Designer. Before painting, the wood is to be sanded, cleaned and coated with an acrylic primer with added oil-based paint. Apply the first coat of putty and coat with oil-based putty, sand the surface and apply the second coat of putty. Paint with an oil-based paint, when dry, sand the surface and apply another coat of oil-based putty. Fine sand and paint using enamel paint.
| Costs shall be charged per m2 | m2 | 148 | 8.4
11.8. | Manufacturing and installation of pine stair stringers 25cm high and 60mm thick
The stringers should be made from first-class dry pine wood, according to the specified details and in all aspects in line with the existing stringers.
| Costs shall be charged per m | m | 8 | 19
11.9. | Manufacturing and installation of pine stair treads
Treads are to be made of first-class dry pine wood, 42 mm thick, and placed according to the design and details and in all aspects in line with the existing staircase.
| Costs shall be charged per m | m | 16 | 22.5
| JOINERY WORKS, TOTAL |  |  |  |  | 0
12 | ROOFING WORKS
12.1. | Procurement and installation of interlocking tiles
Roofing using interlocking tiles with all required shaped pieces and roof guards. Roof guards are to be placed in two rows in a zig-zag pattern next to the eave. Roof tiles must be flat, of high-quality and undamaged.
| Costs shall be charged per m2 of the slanted roof surface | m2 | 250 | 14
12.2. | Procurement and installation of ridge caps
Dry installation of ridge caps with all required fittings and flashings over the ridge batten. Ridge caps should be fixed to the ridge batten with screws. Roof tiles must be flat, of high-quality and undamaged.
| Costs shall be charged per m | m | 16 | 8.5
| ROOFING WORKS, TOTAL |  |  |  |  | 0
13 | METAL WORKS
13.1. | Manufacturing and installation of half round eaves trough made of galvanized sheet metal, 40cm of developed width, with trough width 14cm and thickness 0.60cm
The troughs are to be connected using rivets, in a single line with a maximum spacing of 3cm, and soldered with minimum 40% of tin. Supports for eaves trough are to be made of 25x5mm galvanized flat bars and riveted on the front side with Ø4 mm rivets, with a spacing of 80cm.
| Costs shall be charged per m | m | 32 | 14
13.2. | Manufacturing and installation of galvanized downpipes, 40 cm of developed width, Ø12 cm, made of 0.60 mm thick sheets
Parts of downpipes should enter one another with a minimum overlap of 50mm and soldered with minimum 40% of tin. Galvanized brackets with holders are to be placed 200cm apart. Place decorative strip over the brackets. The distance between the pipes and the wall should be minimum 20mm. The ending of the downpipe should follow the details.
| Costs shall be charged per m | m | 20 | 12.5
13.3. | Flashing of roof edges, drip edges, using galvanized sheet metal, 50 cm of developed width, 0.60 mm thick
Flashing is to be done by covering the entire fascia board.
| Costs shall be charged per m | m | 30 | 7.5
13.4. | Flashing of the valley using galvanized sheet metal, 50cm of developed width, 0.60mm thick
Flashing is to be done in line with the details of the roof tile manufacturer
| Costs shall be charged per m | m | 15 | 7.5
13.5. | Flashing of the chimney using galvanized sheet metal, 50 cm of developed width, 0.60 mm thick
Sheet metal is to be raised minimum 20cm up the chimney wall. Sheet metal edge should be inserted into the brick joint. Flashing of the chimney is to be done in line with the details and instructions of the Designer.
| Costs shall be charged per m | m | 5 | 12.5
13.6. | Manufacturing of the exterior weather drip
The drip is to be made of galvanized sheet metal, 0.60mm thick, with 25cm of developed width. At the window, the sheet metal is to be placed under the window frame, with side edges raised. Drip 4 cm.
| Costs shall be charged per m | m | 16.2 | 8.5
| SHEET METAL WORKS, TOTAL |  |  |  |  | 0
14 | METALWORK
14.1. | Manufacturing and installation of a stair railing made of steel sections and flat bars
The railing is to be made and installed in line with the details and instructions of the Designer. The joints and welds are to be made ideal, cleaned and sanded. Before the installation, the railing is to be cleaned to remove corrosion and dust, sanded and dusted off. Impregnate the railing with a primer and install it. After the installation, repair the primer, apply the first coat of putty, sand the surface, and apply two layers of paint.
| Costs shall be charged per kg | kg | 180 | 4.5
14.2. | Repair of window bars made of steel sections and flat bars
The missing or worn out parts are to be modelled upon the existing ones and thus manufactured and installed, in line with the details and instructions of the Designer. The joints and welds are to be made ideal, cleaned and sanded. Remove old paint using chemical and physical agents, perform sanding and cleaning. Impregnate the bars with a primer and apply two layers of paint for metal.
| Costs shall be charged per m2 | m2 | 7 | 22
| METALWORK, TOTAL |  |  |  |  | 0
15 | PAINTING WORKS
15.1. | Skimming of fine plastered walls and ceilings with a dispersion-based compound
Grind, clean and neutralise surfaces. Inspect and putty minor damages and cracks. Impregnate with a primer and apply dispersion-based compound three times.
| Costs shall be charged per m2 | m2 | 761.05 | 2.2
15.2. | Painting of skimmed walls and ceilings
Procurement of materials and painting of walls and ceilings with semi-dispersion paint in the colour chosen by the Investor, until the entire surface is of a uniform colour.
| Costs shall be charged per m2 | m2 | 761.05 | 2.3
15.3. | Skimming of the facade with a skimming compound
Clean all facade surfaces, removing any deposit. Impregnate the base. The facade is to be skimmed using an exterior skimming compound. All surfaces are to be previously sanded and dusted off. Keep in mind that the skimming compound has the same base as the facade paint.
| Costs shall be charged per m2 | m2 | 192.8 | 2.4
15.4. | Painting of plastered facade with an acrylic paint
Before painting, the facade surface should be sanded and dusted off. Apply the primer and, after it dries, apply the second and third coating, allowing minimum 10-12 hours for drying of each layer. The edges of different colours are to be painted with precision. Plastered surfaces must be completely dry before painting.
| Costs shall be charged per m2 | m2 | 192.8 | 4.7
| PAINTING WORKS, TOTAL |  |  |  |  | 0
16 | MISCELLANEOUS
16.1. | Impregnation of parts of exterior walls
Base preparation, jointing with cement plaster reinforced with fibres, Class R4. In addition to jointing, the plaster is also used to reinforce the Sika Top 122 SP wall. Protective finish coating: transparent hydrophobic impregnation Sikagard 7005.
| Costs shall be charged per m2 | m2 | 105 | 42
16.2. | Installation of water piping
Procurement and installation of water pipes made of crosslinked polyethylene with all required fittings within the piping network. The pipes are designed for pressures ranging from 6 to 10 bar and for water temperatures up to 95ºC. The item includes hanging of pipes onto the wall and the structure, and also cutting of grooves in the wall lining in the area of pipe laying.
| polyethylene PVC pipes DN 20 mm ( 1/2˝) | m | 12 | 5
| DN 25 mm ( 3/4˝) | m | 10 | 6
| DN 32 mm ( 1˝ ) | m | 8 | 7
16.3. | Gate valves
Installation of gate valves on the water installation of sanitary consumers
| On polyethylene PVC pipes DN 20 mm ( 1/2˝) | pcs. | 3 | 14
| DN 25 mm ( 3/4˝ ) | pcs. | 3 | 16
| DN 32 mm ( 1˝ ) | pcs. | 1 | 17
16.4. | Connection to the existing water piping
Construction of the connection to the existing water piping within the existing sanitary block. The item is to include cutting of the existing water pipe and all required work and material for connection. Having supplied the connection, restore everything to its former state.
| Costs shall be charged on a lump sum basis | Lump sum | 1 | 80
16.5. | Pressure testing of the pipeline
Pressure testing of the pipeline. Replace all defective pipes and joints.
| Costs shall be charged on a lump sum basis | Lump sum | 1 | 70
16.6. | Pipeline disinfection
Flushing and disinfection of the pipeline and obtaining of a test certificate from the relevant institution corroborating that the water is bacteriologically safe to drink.
| Costs shall be charged on a lump sum basis | Lump sum | 1 | 300
16.7. | Installation of the drainage system
Procurement and installation of polypropylene drainage pipes including the appropriate fittings. Pipes are to be installed by hanging them on the structure, (using clips with rubber inserts) or embedding them into walls or floors with a minimum designed slope of 2%. This item also includes sealing material for pipe joints.
| DN 50 mm - PVC | m | 6 | 6
| DN 75 mm - PVC | m | 8 | 8
| DN 110 mm - PVC | m | 12 | 13
16.8. | Floor outlets
Procurement and installation of horizontal dry floor outlets with a plastic casing siphon and stainless steel grate. The outlet is to be outfitted with a no-odour siphon insert, without water adding to the siphon.
| Ø 50 mm | pcs. | 2 | 50
16.9. | Sanitaryware
Procurement and installation of sanitaryware
Costs shall be charged per piece
| a. Semi-column wash basin measuring 50x40cm. Installation using anchors fixed to the bearing wall or reinforcements | pcs. | 2 | 100
| b. A toilet with a low flushing valve and floor drain (simplon). The set includes a plastic seat, above-fitted toilet water tank and the supporting pipes | pcs. | 2 | 110
| c. Fayans urinals with concealed siphon | pcs. | 1 | 100
| d. 10l pressure accumulation boiler with a safety valve and Brinox connections | pcs. | 3 | 65
| e. Single lever basin mounted mixer tap | pcs. | 2 | 70
| f. 80x80cm mirror above the washbasin | pcs. | 2 | 40
| g. Liquid soap dispenser with a capacity of 0.6 l. ABS matt-chrome casing. | pcs. | 2 | 50
| h. Two roll horizontal toilet paper holder. ABS matt-chrome casing. | pcs. | 2 | 50
| i. Paper towel dispenser with a capacity of 800 towels. ABS matt-chrome casing. | pcs. | 2 | 70
| j. Wall mounted trash cans with a capacity of 23 litres. ABS matt-chrome casing. | pcs. | 2 | 80
| k. Wall mounted toilet brush. ABS matt-chrome casing. | pcs. | 2 | 40
| l. Wall mounted hangers. A set with three nickel plated hooks. | pcs. | 2 | 35
16.10. | Axial fan
Procurement and installation of an axial fan for extracting air from sanitary blocks Ø100mm, power 60W, with a plastic grille cover
| Costs shall be charged per piece | pcs. | 2 | 15
| MISCELLANEOUS, TOTAL |  |  |  |  | 0
17 | EQUIPMENT AND FURNITURE
Item 101
17.1. | Conference room chair | pcs. | 53 | 33
Metal structure with a seat and back upholstered with an optional fabric.
Item 102
17.2. | Armless task chair | pcs. | 6 | 50
A chair with a plastic base, wheels, lift mechanism and back mechanism, upholstered with an optional fabric.
Item 103
17.3. | Club chair | pcs. | 4 | 100
Dimensions 78x72x65 cm
Structure made of metal and plywood. An armchair with a rounded back and arm supports upholstered with fabric. The seat is cushioned with 6cm thick polyurethane foam.
Item 104
17.4. | Club table | pcs. | 1 | 105
Oval shaped, measuring 60x120cm
Metal structure with the table top made of 10mm thick tempered glass
Item 105
17.5. | Desk | pcs. | 1 | 150
Dimensions 160x80cm
It is made of 25mm thick melamine faced chipboard. It also has sides and a stiffener.
Item 106
17.6. | Conference table | pcs. | 2 | 140
Dimensions 130x70cm
It is made of 25mm thick melamine faced chipboard. It also has sides and a stiffener.
Item 107
17.7. | Folding table | pcs. | 14 | 175
Dimensions 130x70cm
Table top surface: 25mm thick melamine faced chipboard, foldable metal legs.
Item 108
17.8. | Translator’s desk | pcs. | 1 | 130
Dimensions 90x70+55x26cm
It is made of 25mm thick melamine faced chipboard. It fits into the existing recess
Item 109
17.9. | Table for the model | pcs. | 1 | 200
Dimensions 100x150cm
It is made of 25mm thick melamine faced chipboard. Table legs are made of metal box sections
Item 110
17.10. | Double-door wardrobe | pcs. | 6 | 330
Dimensions 80x50x240cm
It is made of 18mm thick melamine faced chipboard. 15cm high skirting, metal legs. In the middle of the wardrobe, there is a space for clothes with a bar and wooden hangers, while above and under it, there are shelves for document storage.
Item 111
17.11. | Movable drawer unit | pcs. | 1 | 70
Dimensions 45x50cm
It is made of 18mm thick melamine faced chipboard. The drawer unit has wheels and 4 drawers
Item 112
17.12. | Wall mounted unit above the desk | pcs. | 1 | 85
Dimensions 35x160x70cm
It is made of 18mm thick melamine faced chipboard. The unit is half-closed with a casement door and has a central shelf
Item 113
17.13. | Wall mounted coat rack | pcs. | 1 | 85
Dimensions 35x160x70cm
Material: 18mm thick melamine faced chipboard with 7 hooks for hanging clothes
Item 114
17.14. | Kitchenette | pcs. | 1 | 1100
Dimensions 60x295cm, height 85cm
It comprises a built-in stainless steel wash basin 50x95cm with a 45x50x18cm bowl, a dish rack and a built-in flat ceramic cooktop measuring 50x30cm with two hot plates. A single-lever tap for hot and cold water shall be installed onto the sink.
Closed wall cabinet, dimensions: 30x355cm, height 75cm, with a middle shelf
Item 115
17.15. | Domestic refrigerator | pcs. | 2 | 450
Dimensions 60x60x140cm
Energy Class A
Item 116
17.16. | Wall stop | m1 | 15 | 10
Width 30cm
Material: 18 mm thick melamine faced chipboard, edged on both sides. Installation: wall anchoring.
Item 117
17.17. | Norwegian radiator | pcs. | 6 | 180
Dimensions 106.5x35cm
Power 1200 W, type Glamox 300I PR 12 ET/DT or similar, parapet mounted.
The price shall include procurement, transport and installation.
| EQUIPMENT AND FURNITURE, TOTAL |  |  |  |  | 0
SUMMARY OF TECHNICAL BUILDING WORKS:
1 | DISASSEMBLY AND DEMOLITION |  |  |  |  | 0
2 | PREPARATION AND EARTHWORKS |  |  |  |  | 0
3 | CONCRETE WORKS |  |  |  |  | 0
4 | MASONRY WORKS |  |  |  |  | 0
5 | REINFORCING STEEL WORKS |  |  |  |  | 0
6 | INSULATION WORKS |  |  |  |  | 0
7 | CARPENTRY |  |  |  |  | 0
8 | PLASTERING
9 | TILING WORKS |  |  |  |  | 0
11 | JOINERY WORKS |  |  |  |  | 0
12 | ROOFING WORKS |  |  |  |  | 0
13 | METAL WORKS |  |  |  |  | 0
14 | METALWORK |  |  |  |  | 0
15 | PAINTING WORKS |  |  |  |  | 0
16 | MISCELLANEOUS |  |  |  |  | 0
17 | EQUIPMENT AND FURNITURE
| WORKS, TOTAL: |  |  |  |  | 0
Jan Pažitnai, BSc in Architectural Engineering

## 2.1.Constr. works on the lock
Design and Construction Supervision Joint Stock Company, I 17 Kralja Petra Boulevard, 21000 Novi Sad, Commercial Account 340-1376-70, TIN SR 101637004, Telephone: 021/477-0096; 444-819, Fax: 021/444-819, Laboratory: 021/6432-821; web site: www.vojvodinaprojekt.rs; е-mail: office@vojvodinaprojekt.rs
pos. | DESCRIPTION OF WORKS | UNIT OF MEASURE | QUANTITY | CENA (eur) | PRICE (RSD) | IZNOS (eur) | AMOUNT (RSD)
CONSTRUCTION WORKS ON THE SHIP LOCK
1 | PREPARATORY WORKS
1.1. | Construction of drainage wells
Construction of drainage wells to lower the water table while the canal lock chambers are being repaired. Well dimensions: Ø225 mm, L=20.00 m. Wells shall be constructed on the left bank, along the chamber wall, at a distance of 5.00 m from the wall. The distance between wells shall be 25.00 m. The item price shall include: Site preparation for construction, transport of the drilling rig, all the equipment, material and tools to the construction site, construction of drainage wells, procurement, transport and installation of filter pack, washing and development of wells. Upon completion of the canal lock repair work, the Supervisor shall specify the well sealing method by giving instructions in writing.
| The calculation shall be made per finished well for the total workmanship and material. | pcs. | 8
1.2. | Water table lowering by drainage wells
Remark:
Water table must be lowered before emptying the lock chambers. Stopping water table lowering - after the lock chambers have been filled with water.
Water table lowering by drainage wells up to the elevation of 73.40. Water table lowering involves continuous operation of pump sets (cca Q=3-7 l/s, max Hs=10.00 m.v.s.) during the execution of works, constantly maintaining the required water table. The Contractor shall provide the pump set, the installation and dismantling thereof, the installation of PVC delivery and gathering pipelines of the required dimensions. Water shall be delivered to the Bega River. Power source, supply and consumption shall be ensured by the Investor. The Contractor shall be responsible for all construction risks and under an obligation to implement occupational safety measures for all the workers, equipment, machines, material and third parties during the execution of works. Assumed water table lowering time: 90 days.
| The calculation shall be made per hour of pump set operation. | hour | 17280 |  |  |  |  | 0
1.3. | Installation of cofferdam beams
Steel beam cofferdams shall be set up in front of the upstream gate and behind the downstream gate of the lock by use of a mobile crane, from the handling platform. Beam dimensions: b/h/L=810/930/10180 mm. A beam shall weigh 3350 kg. There shall be 6 beams in a cofferdam (12 beams altogether). Material, construction and transport of cofferdam beams shall be calculated in the mechanical portion of the design.
| Calculation per hour of mobile crane operation. | hour | 5
1.4. | Water pumping from the canal lock chambers
After the cofferdam is constructed, water shall be pumped by sludge pumps into the Bega River. The item shall include: pump transport, water pumping, as well as all required workmanship and material. Estimated amount of water 10.0*3.0*164.0=4920 m3. Assumed pump capacity 80 l/s.
| Calculation per hour of pump operation. | hour | 20
1.5. | Cleaning the chamber bottom of deposits and sludge
Deposits and sludge shall be broken up by water under pressure and pumped by a sludge pump. The item shall include: cleaning, transport and disposal of sludge in the existing containers on the bank, at a distance of up to 700 m. Estimated amount of sludge 10.0*0.50*164.0=820.0 m3
| Calculation shall be made per m3 of removed deposits and sludge. | m3 | 820
1.6. | Canal bottom cleaning
Canal bottom in the wider floodgate area shall be cleaned by appropriate machinery. The item price shall include: Excavation, transport and disposal of sludge in the existing containers on the bank, at a distance of up to 700 m. Estimated amount of sludge 30.0*100.0*0.50=1500.0 m3
| The calculation shall be made per m3 of the excavated sludge for the total workmanship and material required. | m3 | 1500
1.7. | Construction of cofferdams using jumbo bags
A cofferdam shall be formed of jumbo bags, pyramidal in shape (3+2+1) along the entire width of the lock chamber, on the upstream and downstream side, in order to enable dry working conditions to prepare recesses for the installation of stop logs. The price of this item shall include: placing of sand-filled jumbo bags, placing of PVC foil and removal of the cofferdam after the completion of the recess preparation works and installation of stop logs. Water pumping from the lock chamber by sludge pump and cleaning the chamber bottom of deposits and sludge shall be calculated under items 1.4. and 1.5. Cofferdam dimensions at the upper chamber: h/L=3.00/12.00 m. V=(3*1.00+2*1.00+1*1.00)*12.00*2=144.00 m3 NOTE: The works shall be carried out in the conditions of the natural flow regime of the Bega, at water level 74.40 m a.A.s. (in the period from 15.09. to 01.05.)
| Costs shall be charged per m3. | m3 | 144
| PREPARATORY WORKS, TOTAL |  |  |  |  | 0
2 | DISASSEMBLY AND DEMOLITION
2.1. | Stripping off of reinforced concrete wall lining of the upper lock chamber
Stripping off shall be done by cutting off the edges properly. Upon stripping the lining off, joints shall be cleaned by cramp irons up to the depth of 2 cm and walls shall be washed by water. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill up to 15 km away. The price shall include the required auxiliary scaffolding. Surface area: h*L*2=5.8*99.0*2=1148.40 m2
| Costs shall be charged per m² | m2 | 1148.4 | 39
2.2. | Stripping off of reinforced concrete bridge column lining on the canal lock wall
Stripping off shall be done by cutting off the edges properly. Upon stripping the lining off, joints shall be cleaned by cramp irons up to the depth of 2 cm and walls shall be washed by water. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill up to 15 km away. The price shall include the required auxiliary scaffolding. Column dimensions: b/L/h=2.5/7.5/3.1 m Surface area: (7.5+2.5)*2*3.1=62.0 m2
| Costs shall be charged per m² | m2 | 62 | 39
2.3. | Removal of wooden fender beams
Beams shall be carefully removed together with clips and anchors, loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill. The price shall also include the equipment and machinery required for the execution of works, in line with the Contractor’s technology. NOTE: The overpass works shall be carried out in the conditions of the natural flow regime of the Bega, at water level 74.40 m a.A.s. (in the period from 15.09. to 01.05.).
Costs shall be charged per piece
| a. In the canal lock bed 30*30/400 cm | pcs. | 32 | 8
| b. On the overpass columns 20*20/350 cm | pcs. | 7 | 7
2.4. | Removal of the damaged overpass sections (2 spans)
Overpass columns are made of steel frames encased in a concrete screed. A 12 cm thick concrete pathway leads over them and rests on steel supports. The last two spans have got removed from the design position and are separated from the remaining part of the overpass structure. The item shall include the removal of concrete parts and steel sections. Work shall be carried out from the water (a vessel). Removed material shall be loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km. 2.0*2.70*2*0.12+2.8*3.0*0.2*2=4.7 m3
| Costs shall be charged per m3 | m3 | 4.7 | 120
2.5. | Removal of concrete pathways on the canal lock walls |  |  | 12
Damaged concrete pathway sections on the walls of both lock chambers shall be torn down. The pathway width varies from 1.5m to 4.0m (2.5 m average); thickness 15 cm. Removed material shall be loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km. Estimated extent of damage: 50% 0.5*2*2.5*178.0=445.00 m2
| Costs shall be charged per m2 | m2 | 445 | 8
2.6. | Cement screed removal
The cement screed on the stairs on the right bank slope shall be removed up to the stone stairs and grass and mud shall be removed from the stairs. The debris shall be taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m2 | m2 | 28 | 8.5
2.7. | Removal of the upper layers of abutment walls made of facade brick in flexible mortar
The upper layers of brick shall be removed at a thickness of up to 70 cm. The usable bricks should be cleaned from mortar and stacked at the construction waste dumpsite. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill. The price shall include auxiliary scaffolding too. The amount estimated for removal is 5.0 m3 (the actual amount shall be determined by the Contractor and Supervisor on-site).
| Costs shall be charged per m3 | m3 | 5 | 50
2.8. | Removal of the fence around the plot
The fence shall be carefully removed, cleaned and stacked for reinstallation or loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
Costs shall be charged per m
| a. Wooden posts and wire | m | 50 | 2.5
| b. Metal posts and wire | m | 445 | 5.8
| c. Concrete posts and wire | m | 220 | 4.6
2.9. | Removal of the shiner fence between concrete posts, built in flexible mortar
Bricks should be cleaned from mortar and stacked for rebuilding. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m2 | m2 | 60 | 7
2.10. | Gate removal
The gates shall be carefully removed, usable material shall be cleaned and stacked for reinstallation or loaded onto a truck and transported to a landfill designated by the Investor at a distance of up to 15 km. The debris shall be collected, taken out, loaded onto a truck and transported to a municipal landfill.
| Costs shall be charged per m² | m2 | 17 | 6.4
| TOTAL DISASSEMBLY AND DEMOLITION |  |  |  |  | 0
3 | EARTHWORKS |  |  |  | 0 |  | 0
3.1. | Manual excavation of Class 3 soil for pavements
Manual soil excavation for sideways up to the depth of 10 cm. Cut the edges carefully. Level the excavation bottom. Earth is set aside, at least 2.0 m from the excavation edge.
| Costs shall be charged per m3 | m3 | 13 | 9.5
3.2. | Transport of excess soil from the excavation
Transport of excess soil from the excavation to a landfill at a distance of up to 15km. The precise location of the landfill shall be specified by the Supervisor and the Investor.
| Calculation per m3 of original soil, transported and dispersed at the landfill. | m3 | 13 | 5.5
3.3. | Procurement, transport, dispersal in layers, compacting and fine planning of gravel
Filling of a gravel base under the pavement, free from organic ingredients and impurities. Compacting with adequate compacting tools with 10cm thick layer.
| Costs shall be charged per m3 | m3 | 13 | 22.5
Access roads and handling platforms
3.4. | Marking the access road and handling platform route
| Access road - calculation per m1 (3*80.0=240.00 m1) | m | 240 | 1
| Handling platforms - calculation per m2 (20.0*12.0*2+15.0*14.0=690.00 m2) | m2 | 690 | 1
3.5. | Road and handling platform excavation by trench excavator at road and handling platform width and loading of the excavated material onto transport vehicles. 240.0*3.0*0.60+690.0*0.75=950.00 m3
| Costs shall be charged per m3 | m3 | 950 | 2
3.6. | Roadbed and handling platform subsoil compaction. 240.0*3.00+690.00=1410.00 m2
| Costs shall be charged per m² | m2 | 1410 | 0.5
3.7. | Embankment filling - 30 cm thick layer of sand for the road and 40 cm thick for the platform, with the procurement of material, transport and compaction. 240.0*3.00*0.30+690.0*0.40=492.00 m3
| Costs shall be charged per m3 | m3 | 492 | 10
3.8. | Road and handling platform subgrade planning and rolling.
| Costs shall be charged per m² | m2 | 1410 | 0.5
3.9. | Making a load bearing layer out of mechanically compacted crushed stone aggregate 0-63, with a thickness of 20 cm for the road and 25 cm for the platform, with the procurement of material, transport and compaction. 240.0*3.00*0.20+690.0*0.25=316.50 m3
| Costs shall be charged per m3 | m3 | 316.5 | 30
3.10. | Making a load bearing layer out of mechanically compacted crushed stone aggregate 0-31.5, with a thickness of 10 cm for the road and 10 cm for the platform, with the procurement of material, transport and compaction. 240.0*3.00*0.10+690.0*0.10=141.00 m3
| Costs shall be charged per m3 | m3 | 141 | 30
3.11. | Transport of the excavated material to the local landfill 5.0 to 10 km away.
| Calculation per m3 of the loaded material | m3 | 950 | 3
3.12. | Spreading of the excavated material at the landfill
| Costs shall be charged per m3 | m3 | 950 | 1
3.13. | Cutting trees down and removing stumps.
| Costs shall be charged per piece. (assessed) | pcs. | 10 | 1
| EARTHWORKS, TOTAL |  |  |  |  | 0
4 | CONCRETE WORKS |  |  |  | 0 |  | 0
4.1. | Construction of pathways using concrete grade MB20
Concreting pathways and pavement with concrete grade MB20. The cost shall include all preparation and concreting works, as well as the required formwork. The upper surface should be trowelled. Concrete in 2m sections with pressed joints. After concreting, the concrete maintenance should be provided.
| Costs shall be charged per m2 of the completely built and processed concrete. |  |  | 120
a. | Lock wall pathways, thickness t=15 cm | m2 | 445
b. | Pavements between the canal lock and the existing structures, thickness t=10 cm | m2 | 130
4.2. | Building of MB 20 reinforced concrete stairs on descending stairways to canal
The concreting and installation of stairs at the at the place of existing stairs, with MB20 concrete. The cost shall include all preparation and concreting works, as well as the required formwork. The upper surface should be trowelled. After concreting the stairs, the concrete maintenance should be provided.
| Costs shall be charged per m | m | 10.5 | 25
4.3. | Production of reinforced concrete base, t = 10cm, of middle pillar MB30
Make the formwork and reinforce with Q-503 mesh reinforcement according to design and details. Concrete should be built in and maintained in accordance with regulations. The price includes concrete, formwork and auxiliary scaffolding. The rebars are calculated within a special position. V=(7.5+2.5)*2*3.1*0.10=6.20 m3
| Costs shall be charged per m3 | m3 | 6.2 | 145
4.4. | Rehabilitation of the model threshold of the floodgate on the right bank
Clean the model and remove degraded parts. Hollows should be filled by fine-grained concrete. Cover the exposed surfaces with fine-grained concrete and plaster them. Estimated amount 20.00 m2
| Costs shall be charged per m2. | m2 | 20
TOTAL CONCRETE WORKS
5 | MASONRY WORKS |  |  |  | 0 |  | 0
5.1. | Building of the upper layers of walls made of first class facade brick in flexible mortar, ratio 1:1:6
Whole bricks and halves of straight cut edges should be used for building the lining of the bridge pillar walls. The joints should be formed by using squared or circular iron rod, with a cross section matching the thickness of joints. Layout pattern must be regular. While conducting masonry works, mortar leaking should be prevented. The joints should be treated with cement mortar, ratio 1:2. Grouting and scaffolding are included in the cost.
| Costs shall be charged per m3 | m3 | 5 | 110
5.2. | Laying of a 4 cm thick cement screed over stone stairs
Before laying the screed, the screed substrate should be cleaned and washed. The screed mortar should be prepared with sieved gravel type “One”, ratio 1:3 and maintained it until it hardens. The works include: 4 stairways on the right bank and 1 stairway on the left.
| Costs shall be charged per m2 | m2 | 38 | 7
5.3. | Cleaning of walls of the ship chamber, bank pillars of the bridge, pathway and overpass longitudinal wall with water under high pressure
Cleaning of the walls of the ship chamber bank pillars, pathway and overpass longitudinal wall (bracing) from dirt and degraded parts with water under high pressure (150-200 bar) using an HD device.
Costs shall be charged per m2
| a. Upper chamber - stone lining | m2 | 1148.4 | 21.5
| b. Lower chamber - concrete lining | m2 | 948 | 21.5
| c. Abutments - brick and stone lining Bill of quantities: (4.00*2+6.30)*3.10*2 | m2 | 90
| d. overpass concrete pathway (2.00+0.12)*2*2.70*15=171.72 m2 | m2 | 171.72
| e. longitudinal concrete wall (2*1.00+0.10)*2.70*15=85.05 m2 | m2 | 85.05
The price shall also include the equipment and machinery required for the execution of works, in line with the Contractor’s technology. NOTE: The overpass works shall be carried out in the conditions of the natural flow regime of the Bega, at water level 74.40 m a.A.s. (in the period from 15.09. to 01.05.).
5.4. | Filling the fractures on the pathway of the canal lock
Surfaces to be filled should be cleaned, dedusted and rinsed with water. Fill the joints with hot bitumen 70/100. Avoid material leaking and walls dirtying. Estimated extent of damage: 20% 0.2*2*2.5*178.0=178.00 m2
| Costs shall be charged per m2 | m2 | 178 | 4.5
5.5. | Grouting the walls of the upper chamber of the canal lock and the abutments
FIll the cleaned joints well with the grouting mass and treat them. The grouting mass must not be of low density to avoid material leaking and dirtying of stones and bricks. After grouting, clean the joints and face. Grouting material Sikadur 31 CF or other adequate material.
Costs shall be charged per m2
| Upper chamber - walls with stone lining | m2 | 1148.4 | 102
| Abutments - brick and stone lining | m2 | 90
102
5.6. | Replacement of damaged stone parts of the upper chamber
Damaged stone wall parts should be removed and built with new stone. The masonry stone must be in proper condition. The rows should be built according to the current state, with proper bonding. Before being placed, the stone is wetted with water. After finishing the building, clean the stone and joints. The price includes: demolition and removal of damaged stone, procurement, transport, processing and building, as well as auxiliary scaffolding.
Costs shall be charged per m3
| Upper chamber - estimated: 20.00 m3 | m3 | 20 | 327
5.7. | Repair of overpass pillars, pathway and longitudinal wall and the damaged parts of the lower (concrete) chamber with repair cement mortar
Clean the concrete surfaces to be repaired, dedust and rinse them with water. Cracks should be filled and processed well. The repair mass must not be of low density in order to avoid leakage of material and dirtying of the overpass pillars and the chamber walls and bottom. After applying the mortar, clean the concrete surfaces. Work on the overpass pillars and lower pathway surface is performed from water (from a vessel), and that on the walls of the chamber from the auxiliary scaffold. Repair material: Durocret-plus, Sika MonoTop 622 Evolution or other appropriate material. Costs shall be charged per m2
| Overpass pillars - surface: 2.80*2.75*2*15=231.00 m2 | m2 | 231 | 3.5
| Overpass pathway - surface: (2.00+0.12)*2*2.70*15=171.72 m2 | m2 | 171.72
| Longitudinal wall - surface: (2*1.00+0.10)*2.70*15=85.05 m2 | m2 | 85.05
| Lower chamber - estimated surface (10%). (2*6.0+10.0)*79.00*0.10=174.00 | m2 | 174
The price shall also include the equipment and machinery required for the execution of works, in line with the Contractor’s technology. NOTE: The overpass works shall be carried out in the conditions of the natural flow regime of the Bega, at water level 74.40 m a.A.s. (in the period from 15.09. to 01.05.).
5.8. | Grouting joints and repair of cracks with repair cement mortar
Grout the joints on the concrete protection of the canal bank. Surfaces to be grouted should be cleaned, dedusted and rinsed with water. The substrate should be well cleaned before applying mortar. Joints should be filled and processed well. The grouting mass must not be of low density to avoid material leaking and dirtying of the lining. After grouting, clean the joints and face. Repair material: Durocret-plus, Sika MonoTop 622 Evolution or other appropriate material. Estimated extent of damage: 50% 0.5*(70.0+30.0)*10.0=500.00 m2
| Costs shall be charged per m2 | m2 | 500 | 3.5
5.9. | Repair of minor damages on the concrete pathway with repair cement mortar
Repair smaller damages (holes) on concrete pathsway. Surfaces to be repaired should be cleaned, dedusted and rinsed with water. The damaged places be filled and processed well. Upon completing the repair, clean the surfaces. Estimated extent of damage: 10% 0.1*2*2.5*178.0=89.00 m2 Repair material: Durocret-plus, Sika MonoTop 622 Evolution or other appropriate material.
| Costs shall be charged per m2 | m2 | 89 | 84
5.10. | Repair of walls and the lower plate of the concrete chamber with penetrant
Repair the walls and the lower plate of the lower chamber with three coatings. The price includes the substrate preparation and auxiliary scaffolding. Repair material: Aquamat penetrant for concrete or another appropriate penetrant. (2*6.0+10.0)*79.0=1738.00 m2
| Costs shall be charged per m2 | m2 | 1738 | 15
5.11. | Construction and placing of the fence of steel galvanized pipes (pillars) and plasticized mesh of 2.0m height
Building of the protective fence around the canal lock complex of steel galvanized pipes and mesh of 2.0m height. The price includes manual excavation of soil, concreting of pillar foundations 20x20x80cm with sloping edges, installation of anchor plates and procurement and mounting of pillars and mesh.
| Costs shall be charged per m | m | 715 | 35
5.12. | Construction and mounting of a gate made of galvanized pipes and plasticised mesh
Construction of gates of galvanized steel pipes and grids mesh with a height of 2.0m. The price includes manual excavation of soil, concreting of pillar foundations 20x20x80cm with sloping edges, installation of anchor plates and procurement and mounting of gates.
Costs shall be charged per piece
| a. Double-winged 2x1.8m | pcs. | 2 | 85
| b. Single-winged 1m | pcs. | 4 | 60
TOTAL MASONRY WORKS
6 | REINFORCING STEEL WORKS |  |  |  | 0 |  | 0
6.1. | Rebars installation
Procurement, cutting, bending and installation of rebars. Price includes all necessary works and materials.
Calculation per kg of installed rebars.
| MAG 500/560 | kg | 700 | 1.1
| B500B (RA 400/500) | kg | 200 | 1.1
TOTAL REINFORCING STEEL WORKS
7 | INSULATION WORKS |  |  |  | 0 |  | 0
7.1. | Impregnation of surfaces
Apply the impregnation agent on the repaired and cleaned surfaces. Before applying a hydrophobic coating, the surface must be dry, free from damp parts. Protective coating: transparent hydrophobic impregnation Sikagard 700 or other, suitable coating. Application with brush, paint roller or spray, in two layers.
Costs shall be charged per m2
| a. Upper chamber - wall - stone lining | m2 | 1148.4 | 33.5
| b. Lower chamber - wall - concrete lining | m2 | 948 | 33.5
| c. Abutments - brick and stone lining | m2 | 90
| d. staza estakade - od betona (2.00+0.12)*2*2.70*15=171.72 m2 | m2 | 171.72
| e. podužni zid - od betona (2*1.00+0.10)*2.70*15=85.05 m2 | m2 | 85.05
| f. lining of overpass columns - concrete 2.80*2.75*2*15=231.00 m2 | m2 | 231
INSULATION WORKS, TOTAL
8 | CARPENTRY |  |  |  | 0 |  | 0
8.1. | Replacement of worn-out and damaged wooden bumpers on overpass
Procurement of materials making and replacement of worn and damaged bumpers, dimensions 20x20 / 350cm. New elements should be made of dry pine wood modelled on the disassembled elements, processed and installed with all required connections, brackets and anchors. Work shall be carried out from the water (a vessel). Total of 15 bumper beams.
| Costs shall be charged per m3 | m3 | 2.1 | 18
8.2. | Replacement of worn-out and damaged wooden bumpers on ship chamber
Procurement of materials making and replacement of worn and damaged bumpers, dimensions 30x30/400cm. New elements should be made of dry pine wood modelled on the disassembled elements, processed and installed with all required connections, namely metal brackets. Wooden bumpers are placed at 10.0 m. The price shall include auxiliary scaffolding too. Total of 30 bumper beams.
| Costs shall be charged per m3 | m3 | 10.8 | 36
CARPENTRY, TOTAL
9 | METALWORK |  |  |  | 0 |  | 0
9.1. | Removal of the old paint and painting the steel sheet protection of edges with metal paint
Before painting, remove old paint and corrosion by chemical and physical materials, grind and clean. Apply the base paint to the steel carriers and paint twice with metal paint.
| Costs shall be charged per m2 | m2 | 72 | 4.4
9.2. | Removal of the old paint and painting steel manhole covers
Before painting, remove old paint and corrosion by chemical and physical materials, grind and clean. Apply the base paint to the steel carriers and paint twice with metal paint.
| Costs shall be charged per m2 | m2 | 8 | 3.4
9.3. | Removal of old paint and painting of the steel fence on the wall of the canal lock and overpass
Before painting, remove old paint and corrosion by chemical and physical materials, grind and clean. Apply the base paint to the steel carriers and paint twice with metal paint. Total fence length 178.0+15*2.70=218.50 m1. Estimated extent of damage 10%.
| Costs shall be charged per m1 | m1 | 21.85 | 4.8
9.4. | Repair of ladders in the canal lock
Dismantling of ladders in the canal lock, cleaning from corrosion and remounting. Before painting, remove old paint and corrosion by chemical and physical materials, grind and clean. Apply the base paint to the steel carriers and paint twice with metal paint. After ladders are repaired conduct remounting. Dimensions of ladders b/h=60/550 cm.
| Costs shall be charged per piece. | pcs. | 6 | 75
9.5. | Threshold lining at the canal lock chamber gate
Vertical and upper surface of the gate threshold should be paved with 10 cm thick stainless steel sheets. Unfolded sheet metal width 64 cm: B=250+150=400 mm. Length of lining on gate threshold L=2*5800=11600 mm. The lining material is stainless steel EN 1.4301 (X5CrNi18-10), in accordance with BS EN 10088. After welding, pickling of the welded joints and the surrounding area and passivization should be performed. The lining is fastened to the chamber bottom with the anchors welded to sheet metal on the lower side. When placing the lining, the anchors should be set into pre-drilled holes in concrete, filled with anchoring mass of Sika AnchorFix or other suitable mass. The contact surface of the lining and the existent construction should be coated with permanent elastic sealing agent on polyurethane basis (Sikafex Pro 2HP or other suitable agent). Lining is placed on the threshold of upper and middle gate. G=0.40*5.80*2*0.01*7850*2=728.48 kg
| Costs shall be charged per kg of material. | kg | 728.48
9.6. | Lock gate upper bearing recess
Form a new recess in the existing recess for the gate upper bearing according to the details given in the mechanical part of the project. The item shall include: removal of the existent upper bearing, preparation of space for placing of 2 bearing pillars of IPB200 profiles, length 1230 mm, concreting around bearing pillars with fine-grained concrete MB 30. The pillar calculation is in the mechanical part of the project. Dimensions of recess for one bearing pillar: 40x40/105 cm. 8 pillars for 4 bearings (two on upper and middle gate). V=0.40*0.40*1.05*8=1.34 m3
| Costs shall be charged per m3 of concrete. | m3 | 1.344
9.7. | Recess with gate side support
Form a new recess in the existing recess of the side support of the gate according to the details given in the mechanical part of the project. The item shall include: removal of the existent side support, preparation of space for placing new side support, filling fine-grained concrete MB 30 (as necessary), construction of abutments of full profile steel 100x150/50 mm, welded to anchor plate 200x170/10 mm, with 2 holes for M16 anchor-bolts with nuts, drilling of 2 holes for M16 anchors, filling the anchoring mass of Sika AnchorFix type or other suitable mass and installation of threaded anchors. Material of side support is stainless steel EN 1.4301 (X5CrNi18-10), in accordance with BS EN 10088. Upper gate has two side supports per one gate leaf. Middle gate has two side supports per one gate leaf. Total: 2*2+2*3=10 side supports. Note: difference between dimensions of the upper and middle gate recesses is insignificant. G=(0.10*0.15*0.05+0.20*0.17*0.01)*7850*10=85.57 kg
| Costs shall be charged per kg of material. | kg | 85.565
9.8. | Lining of the vertical edge at gate recess
Covering the recess vertical edge with 10 mm thick stainless steel sheet. Sheet unfolded width: for upper gate B=150+200=350 mm, for middle gate B=210+290=500 mm, length 5800 mm. The lining material is stainless steel EN 1.4301 (X5CrNi18-10), in accordance with BS EN 10088. The lining is fastened to the chamber wall with the anchors welded to sheet metal on the lower side. When placing the lining, anchors should be put into the pre-drilled holes in the chamber wall, filled with the anchoring mass of Sika AnchorFix type or other suitable mass. The contact surface of the lining and the existent construction should be coated with permanent elastic sealing agent on polyurethane basis (Sikafex Pro 2HP or other suitable agent). Lining is placed on 4 vertical edges (two on upper and middle gate). G=(0.35+0.50)*5.80*2*0.01*7850=774.01 kg
| Costs shall be charged per kg of material. | kg | 774.01
9.9. | Stop log threshold
Making of the threshold for support of stop logs on chamber bottom. The threshold is made of stainless steel of 130x10 mm, length L=200+10000+200=10400 mm. The threshold material is stainless steel EN 1.4301 (X5CrNi18-10), in accordance with BS EN 10088. The threshold is fastened to the bottom slab of the lower chamber with the anchors welded to the threshold sheet metal on the lower side. When placing threshold, anchors should be put into the pre-drilled holes in the chamber bottom, filled with the anchoring mass of Sika AnchorFix type or other suitable mass. The contact surface of the threshold and the existent construction should be coated with permanent elastic sealing agent on polyurethane basis (Sikafex Pro 2HP or other suitable agent). Threshold is placed in front of the upper and behind the lower gate. G=0.13*0.01*10.40*2*7850=212.26 kg
| Costs shall be charged per kg of material. | kg | 212
9.10. | Lining of the stop log recess
Form a new recess in the stop logs’ recess of the side support of the gate according to the details given in the mechanical part of the project. The position includes: the preparation for the making of the recess of envisaged dimensions, filling fine-grained concrete MB 30 (as necessary) and placing 10 mm thick stainless steel lining on the recess. Unfolded sheet metal width 64 cm: B=100+260+370+260+100=1090 mm, length 5800 mm. The lining material is stainless steel EN 1.4301 (X5CrNi18-10), in accordance with BS EN 10088. The lining is made in three parts (two side and one frontal). Every part of the lining is fastened to the recess wall with the anchors welded to sheet metal on the lower side. Weld the sheet metal 120x10 mm, length 5800 mm, on the upstream side part of the lining, on which the stop log spring slides. Weld the sheet metal 130x10 mm, length 5800 mm, on the downstream side part of the lining, on which the side rubber gasket of the stop logs slides. Frontal guide, dimensions 27x35 mm, length 5800 mm, should be welded on the frontal part of the lining. When placing the lining, the anchors should be set into pre-drilled holes in recess wall, filled with anchoring mass of Sika AnchorFix type or other suitable mass. The contact surface of the lining and the existent construction, as well as the joints of lining parts, should be coated with permanent elastic sealing agent on polyurethane basis (Sikafex Pro 2HP or other suitable agent). Lining is placed in 4 recesses (two in front of the upper and behind the lower gate). G=((1.09+0.13+0.12)*0.01+0.027*0.035)*5.80*4*7850=2612.51 kg
| Costs shall be charged per kg of material. | kg | 2613
METALWORK, TOTAL
10 | OTHER WORKS |  |  |  | 0 |  | 0
10.1. | Piezometer installation
Procurement and installation of piezometers for monitoring of groundwater level.
| Costs shall be charged per piece of installed piezometer. | pcs. | 2 | 20000
10.2. | Repair of the embankment protective slope
Construction of a stone lining made of broken stone, fraction of 15-30 cm with manual stacking - rolling with thickness of 40 cm.
| Costs shall be charged per m3 | m3 | 20 | 42
TOTAL OTHER WORKS
SUMMARY OF WORKS ON CANAL LOCK:
1 | PREPARATORY WORKS |  |  |  |  | 0
2 | DISASSEMBLY AND DEMOLITION |  |  |  |  | 0
3 | EARTHWORKS |  |  |  |  | 0
4 | CONCRETE WORKS |  |  |  |  | 0
5 | MASONRY WORKS |  |  |  |  | 0
6 | REINFORCING STEEL WORKS |  |  |  |  | 0
7 | INSULATION WORKS |  |  |  |  | 0
8 | CARPENTRY |  |  |  |  | 0
9 | METALWORK |  |  |  |  | 0
10 | OTHER WORKS |  |  |  |  | #REF!
TOTAL:
PRICES ARE WITHOUT VAT
Novi Sad, November 2018
Prepared by:
Jelena Solaković, B.Sc.C.E.
VOJVODINAPROJEKT

## 4.1.El.works- power cables
Item | ITEM DESCRIPTION | Unit of measurement | Quantity | Unit price RSD | Total RSD
ELECTRICAL WORKS
I | POWER CABLES AND OUTDOOR LIGHTING
THE PRICED BILL OF QUANTITIES INCLUDES:
Procurement, transport and storage of materials, tools and equipment at the construction site, in line with the specific items.
Delivery of all materials stated under certain items and all small non-specified materials required for quality and complete installation.
Installation and connection fully in accordance with what is stated in certain positions in accordance with the relevant regulations and rules of quality installation
Testing and commissioning of the already completed installations.
Restoring the proper condition of all potentially damaged places for the already performed works.
All materials used have to be in accordance with the effective Serbian regulations and of 1st class quality.
All works must be performed by professional workers and fully in accordance with the applicable Serbian regulations for relevant works.
The calculation is given per unit of measurement of the completed position.
Finishing works and handover of the installation to the investor.
1. | CABLES
GENERAL PROVISIONS: Positions include delivery, transportation, storage on construction site, cable laying by description in items, cable ending and connection, test, voltage release and warranty period according to the Agreement with the Investor.
1.1 | 1kV CABLES
Distribution cabinet power supply cables. The cables are placed into a trench dug in advance (from STS switch panel). The cables are of the type and cross section as follows, with copper wires and insulation made of polyethylene mesh:
| PP00 4x16mm2 from STS distribution cabinet to OMM technical building | m | 75
| PP00-Y 3x2.5mm2 from STS distribution cabinet to Traffic light distribution cabinet | m | 35
1.2. | POWER SUPPLY CABLES FOR EXTERNAL AND SIGNAL LIGHTING
The item includes the connection between the distribution cabinet and external lights. The cables are laid into the trench prepared in advance through the PVC hoses placed in advance. Cable extraction and laying included.
The cables are with copper wires and PVC insulation of the type and cross section as follows.
| PP00-Y 3x1,5mm2 from Traffic light distribution cabinet to SF.N and SF.U | m | 260
| PP00-Y 3x2,5mm2 from S4.L pillar to FL1 ÷ FL4 | m | 55
| PP00 4x4mm2 from STS switch cabinet to S10.L pillars; S11.L and S12.L | m | 85
TOTAL 1:
2. | PVC AND METAL PIPES
2.1 | PVC PIPES
Delivery, transport and installation in walls, as a protection for bringing cables into the facility, for the below PVC pipes.
Per meter of pipes:
|  50mm for introducing power supply cable | m | 12
2.2. | Delivery, transport and installation of the pipes stated below for protection of cables for laying under bridge steel construction.
Per meter of pipes:
| Æ1" | m | 35
| Æ2" | m | 45
TOTAL 2:
3 | ADDITIONAL EARTHING FOR EXTERNAL LIGHTING
3.1. | Delivery and laying into the already excavated trench, in parallel with power supply cables for external lighting, of zinc ribbons Fe/Zn 25x4mm, already used for additional earthing, i.e. for protection of pillars from atmospheric discharge.
| Total for work, materials and transport. | m | 140
3.2. | Set for connecting the pillars with additional earthing comprising approximately 1.5m of Fe/Zn strip 20x3mm and one crossing piece
| Total for work, materials and transport. | pcs. | 6
TOTAL 3:
4 | LIGHTS
Lights are installed with lamp holders, bulbs and fluorescent tubes, starters, control gears, lighters and other equipment required for quality operation of lamps.
4.1 | Light for urban surrounding with aluminium alloy housing cast under pressure, protector and polycarbonate cover, mirrors of electropolished and anode protected aluminium of high purity and the control gear, equivalent to type K-LUX/1640/100 MINEL SCHREDER, with high pressure sodium lamp 100W, 230V, 50Hz, IP66, IK09
| Lamp connection and installation. | pcs. | 13
4.2 | Surface-mounted lamp with housing and transparent diffusor made of injected, UV stabilised, B2 self-extinguishing, halogen-free polycarbonate, polyurethane watertight gasket and parabolic, bright reflector,equivalent of TITAN BS, BUCK, 1xT26 36W, G13, IP65, 230V. The lamp should be equipped with light source - fluorescent tube lights T5, 36W, 4000K, Ra>80, of high efficiency (HE) up to 104lm/W.
| Lamp connection and installation. | pcs. | 4
4.3 | Traffic light - one two-part driver lantern, diameter Ø300mm, LED red and green.
| Lamp connection and installation. | pcs. | 2
TOTAL 4:
5 | LIGHT POLES
5.1 | Conic light pole, 4m high, Ø60mm on pole tope with the base of min. 400×400×10mm, with Ø90mm opening, protected by warm internal and external zinc plating and additional anti-corrosion protection up to 40cm above the foundation base. The pole should be completely equipped with: - carrier and connection panel RPO-4 - fuse FRA 16/6A or automatic switch B 6A, 1 piece. - power supply cable for lamp PP00-Y 3×1.5mm2, 4m, - zinc bolt for earthing and on the pole, - cover with a red arrow (lighting symbol), - protection of connection area from rain, - ordinal number of the pole.
| Pole delivery and installation | pcs. | 13
5.2 | Traffic light pole, 3.2m high, Ø60mm on pole tope with the base of min. 400×400×10mm, with Ø90mm opening, protected by warm internal and external zinc plating and additional anti-corrosion protection up to 40cm above the foundation base. The pole should be completely equipped with: - carrier and connection panel RPO-4 - fuse FRA 16/6A or automatic switch B 6A, 1 piece. - power supply cable for lamp PP00-Y 3×1.5mm2, 4m, - zinc bolt for earthing and on the pole, - cover with a red arrow (lighting symbol), - protection of connection area from rain, - ordinal number of the pole.
| Pole delivery and installation | pcs. | 2
5.3 | Rubber base for pole levelling, similar to type PEPLIC-REASU, "SOGEXI", dim. 400×400×10mm, fully made in accordance with manufacturer0’s specifications. The rubber pad is placed on the concrete foundation under the base of the pole. The surface of the pad is with grooves so that it enables draining of water.
| Delivery and placing of rubber pads | pcs. | 15
TOTAL 5:
6 | SWITCH CABINETS
Delivery, transport, installation and voltage release for the below cabinets:
The housing of the distribution cabinet is made of steel sheet metal protected with anti-corrosion paint. The housing has a door, lock and a key. Envisaged in the cabinet is the construction for carrying equipment made of perforated profiles.
Placed above the equipment is a protective plate. The housing of the cabinet is visibly bridged with protective rail (earthing) and the door is bridged with copper braid.
The cabinet protection against humidity and external objects is of IP-55 class.
The item includes all required materials, wires for wiring, plastic canals, clamps, rails for connecting neutral lines, rails for connecting protective lines, marking numbers etc.
6.1 | Distribution cabinet - Traffic light - with the following equipment:
One-pole rotary cam switch 1.2 for installation on the door, similar to K1B-011ULH “Merlin Gerin” type - 2 pcs.
One-pole installation automatic switch C60N, 1P, 10A, characteristics C, 6kA - 2 pcs.
Red LED signal lights; 230V, 50Hz; installation into panel, Ø22mm - 2 pcs. Type: Schneider Electric XB4 BW34M5.
Green LED signal lights; 230V, 50Hz; installation into panel, Ø22mm - 2 pcs. Type: Schneider Electric XB4 BW33M5.
Other small non-specified materials: copper buses, cable glands and terminals, spacing insulators, bolts, connection clamps etc.
| Paid per cabinet | pcs. | 1
TOTAL 6:
7 | FINAL WORKS AND HANDOVER OF INSTALLATIONS TO INVESTOR
7.1 | After completing the works on the above installations, the contractor is obliged to perform the following:
- patching walls at places of penetration of installations
- removal of potential technical, aesthetic faults of the installations in the facility
- cleaning debris from premises and disposal of debris out of the facility.
Upon the completion of the inspection of the conducted works all examinations envisaged by regulations should be carried out, including:
- measuring the resistance of the cable insulation, electrical equipment and appliances of individual and overall installations
- testing the functionality of certain devices and equipment, as well as the functionality of overall installations,
- verifying the protection from touch voltage in installation,
- measuring voltage drops on consumer connection
- measuring earthing transition resistances etc.
After performing the measuring the contractor shall make a protocol and submit to the Investor all required certificates with the verification of the obtained results.
The contractor is obliged to provide a written guarantee in accordance with the relevant SRPS regulations and the existent contractual obligations for all conducted works and the installed materials procured by it for the purpose of this installation.
The contractor is also obliged to issue of all required instructions for subsequent maintenance.
| TOTAL 7: | lump sum
8 | CONSTRUCTION WORKS
8.1. | Testing and excavation of trench of dimensions 0.4x0.8m in soil planned up to the future elevation of terrain. Forming of cable bed of two layers of small grained land of 0-4mm size or pure river sand of 10 cm layer thickness, placing PVC protection 10 cm above the cable and a PVC tape 40 cm above cable, backfilling of trench with selected soil from the excavation without rock or organic substance contents, in layers of 15 cm with compaction with a vibrating compactor in two layers, each with two passes and the transport of excess material to a landfill determined by the Supervisory Body for low civil engineering, but not farther than 1000 m in one direction.
| Total for work, materials and transport. | m. | 250
8.2. | Laying protective PVC pipes Æ 110 mm at locations of crossing with other installations. Pipes are laid in an excavated trench envisaged by the preceding item. Pipes are backfilled with sand with 15cm overlayer. The next backfilling layers are the same as described in positions for cable trenches.
| Total for work, materials and transport. | m | 10
8.3. | Delivery and placing of the cable trace mark, underground cables and cable sets and canals with the data according to ED regulations.
| Total for work, materials and transport. | pcs. | 15
8.4. | Excavation of the trench for the foundation of the light pole and distribution cabinet -Traffic light, dimensions 600x600x800mm. Making of the concrete MB20 foundation with placing of all required elements such as anchor, bolts, anchor board, bolts and washers, PVC pipes ø75mm for cable entry-exit, as well as the required number of patterns for bolt centering.
| Total for work, materials and transport. | pcs. | 3
8.5. | Overview of completed works | lump sum
TOTAL 8:
9 | OVERVIEW AND REVISION OF THE POWER FACILITY OF THE TRANSFORMER STATION
Types of overviews and works
9.1 | Energy transformer
9.2 | MV and LV Block
9.3 | Control, measurement and adjustment of protection
9.4 | Construction part
9.5 | Expert findings
Expert findings on the inspection and revision of the transformer station with the report on the measurement of insulation resistance of the transformer primary and secondary windings, and on the state and extent of protection. Report on the measurement of earthing resistance in the transformer station and the measurement of continuity.
| TOTAL 9: | lump sum
RECAPITULATION - POWER CABLES AND OUTDOOR LIGHTING:
1 | CABLES
2 | PVC AND METAL PIPES
3 | ADDITIONAL EARTHING FOR EXTERNAL LIGHTING
4 | LIGHTS
5 | LIGHT POLES
6 | SWITCH CABINETS
7 | FINAL WORKS AND HANDOVER OF INSTALLATIONS TO INVESTOR
8 | CONSTRUCTION WORKS
9 | OVERVIEW AND REVISION OF THE POWER FACILITY OF THE TRANSFORMER STATION
10 | REMOVAL OF THE EXISTENT INSTALLATION AND EQUIPMENT
TOTAL - POWER CABLES AND OUTDOOR LIGHTING:

## 4.2.El.works techn.building
Item | ITEM DESCRIPTION |  | Unit of measurement | Quantity | Unit price in RSD | Total RSD
ELECTRICAL WORKS
II TECHNICAL BUILDING
I ELECTRICAL INSTALLATIONS
1 | Delivery and installation of polyester distribution cabinet GRO for installation into wall. The cabinet dimensions are 600×400×200mm (W×H×D), with IP54 protection class. The following certified equipment is installed in GRO:
Protective device with differential electricity 40/0,3A, 4p - 1 piece.
Three-pole switch similar to type NG125 N 3P 40 C, with nominal current of 40A, with short-circuit protection and overload protection - 1 piece.
One-pole installation automatic switch C60N, 1P, 6A, characteristics C, 6kA - 1 piece.
One-pole installation automatic switch C60N, 1P, 10A, characteristics C, 6kA - 5 pcs.
One-pole installation automatic switch C60N, 1P, 16A, characteristics C, 6kA - 13 pcs.
Three-pole installation automatic switch C60N, 3P, 16A, characteristics C, 6kA - 1 piece.
| all mounted on the insulation board, connected, tested and commissioned for functional operation. All equipment in the cabinet should be marked clearly and visibly. The cabinet must have a one-pole as is drawing and possess a type certificate. |  | set | 1
2 | Delivery and installation of a standard polyester measuring-distribution cabinet OMM for outdoor installation into wall, with IP54 protection class. The following certified equipment is installed in OMM:
Three-phase, two-tariff electricity meter for measuring power consumption 10-40A - 1 piece.
Electricity meter 230V, 10A - 1 piece
One-pole installation automatic switch C60N, 1P, 32A, characteristics C, 6kA - 3 pcs.
One-pole installation automatic switch C60N, 1P, 40A, characteristics C, 6kA - 3 pcs.
| all mounted on the insulation board, connected, tested and commissioned for functional operation. All equipment in the cabinet should be marked clearly and visibly. The cabinet must have a one-pole as is drawing and possess a type certificate. |  | set | 1
3 | Procurement and making of the supply line for bulbs, conductor N2XH-2,3,4x1,5mm2, on the wall, under plaster, with excavation of canals and restoring the original condition, with average conductor length of 8m. |  | pcs. | 28
4 | Procurement and making of the supply line for single-phase Schuko socket, conductor N2XH-3x2.5mm2, in the wall, under plaster, with excavation of canals and restoring the original condition, with average length of 9m. |  | pcs. | 22
5 | Procurement and making of the supply line for three-phase Schuko socket, conductor N2XH-5x2.5mm2, in the wall, under plaster, with excavation of canals and restoring the original condition, with length of 19m. |  | pcs. | 1
6 | Delivering, installing and connecting a single-phase sockets with protective contact, for installation on wall, 16A, 250V, modular version. The item includes also suitable installation boxes for installation and the required auxiliary installation tools.
| - module with one socket |  | pcs. | 6
| - module with two sockets |  | pcs. | 14
7 | Delivering, installing and connecting a single-phase Schuko socket with a lid, 16A, 230V, IP43, for mounting on wall. |  | pcs. | 2
8 | Delivering, installing and connecting three-phase five-pole socket 16A, 400V, for installation on wall. |  | pcs. | 1
9 | Delivery, installation and connecting of installation switches for lighting, modular version, 10A, 250V, for installation on wall. The item includes also suitable installation boxes for installation and the required auxiliary installation tools. Grouping of modules is done submitted lighting base.
| module with ordinary switch |  | pcs. | 6
| module with a multiway switch |  | pcs. | 8
| module with serial switch |  | pcs. | 2
| module with toggle switch with indicator |  | pcs. | 1
10 | Procuring, installing and connecting lamps with all elements required for functional operation.
| Type A - Mounted lamp equivalent to ORIEN DL 424, BUCK, 4xT16 24W, G5, IP20, 230V. Lamp housing made of steel sheets of 0.6 mm thickness. The lamp should be equipped with light source - fluorescent tube lights T5, 24W, 4000K, Ra>80, of high efficiency (HE) up to 104lm/W. Optical equipment of the lamp, matt "dark light", aluminium, double-parabola. Glare limitation according to EN 12464 - UGR < 19, L ≤1.000 cd/m². The lamp is delivered along with the electronic control gear of A2 class, made by renowned producers (Osram, Philips, Vossloh Schwabe), installation kit and light source T5, 24W (Philips, Osram). |  | pcs. | 12
| Type B - Mounted lamp equivalent to ORIEN DL 228, BUCK, 2xT16 28W, G5, IP20, 230V. Lamp housing made of steel sheets of 0.6 mm thickness. The lamp should be equipped with light source - fluorescent tube lights T5, 28W, 4000K, Ra>80, of high efficiency (HE) up to 104lm/W. Optical equipment of the lamp, matt "dark light", aluminium, double-parabola. Glare limitation according to EN 12464 - UGR < 19, L ≤1.000 cd/m². The lamp is delivered along with the electronic control gear of A2 class, made by renowned producers (Osram, Philips, Vossloh Schwabe), installation kit and light source T5, 28W/840 (Philips, Osram). |  | pcs. | 3
| Type C - Mounted lamp with compact fluorescent lamp FWG201 2×PL-C/4P18W HF WH, equivalent of GONDOLA, IP65, Philips. |  | pcs. | 8
| Type D - Mounted lamp with bulb 2×40W, similar to type 746 OBLO, IP40, Buck. |  | pcs. | 3
| Type E - Mounted panic light 1×8W, with 3h autonomy, equivalent to BPN P 108, IP40, Buck. |  | pcs. | 4
11 | Removal of the existent installation and installation equipment and handover to the Investor |  | lump sum
12 | Reception-finishing works,costs of material procurement and transport. |  | lump sum
13 | After completing the works on the above installations, the contractor is obliged to perform the following:
- patching walls at places of penetration of installations
removal of potential technical, aesthetic faults of the installations in the facility
- cleaning debris from premises and disposal of debris out of the facility.
Upon the completion of the inspection of the performed works all examinations envisaged by regulations should be carried out, including:
- measuring the resistance of the cable insulation, electrical equipment and appliances of individual and overall installations
- testing the functionality of certain devices and equipment, as well as the functionality of overall installations,
- verifying the protection from touch voltage in installation,
measuring voltage drops at consumer connection
- measuring earthing transition resistances etc.
After performing the measuring the contractor shall make a protocol and submit to the Investor all required certificates with verifications of the obtained results.
The contractor is obliged to provide a written guarantee in accordance with the relevant SRPS regulations and the existent contractual obligations for all conducted works and the installed materials procured by it for the purpose of this installation.
| The contractor is also obliged to issue of all required instructions for subsequent maintenance. |  | lump sum
TOTAL - I ELECTRICAL INSTALLATIONS
II LIGHTNING INSTALLATIONS
1 | Delivery of materials and making the foundation earthing with zinc ribbon FeZn 25x4mm/78m, laid in the trench around the facility, with the main earthing connection, in a typical box with bonding material. |  | set | 1
2 | Route survey and excavation of a 0.4x0.8m trench in the soil planned up to the future ground level and trench backfilling with select excavation soil containing no stone or organic matter, with compaction by vibrating tamper in two layers with two passes each and transport of excess material to a landfill to be designated by the Supervisor for civil engineering construction but not further than 1000m away in one direction. |  | met | 83
3 | Delivery and installation of the line P FeZn 25x4mm/3,5met SRPS N.B4.901 Č, for the installation of earth connection for MS. |  | pcs. | 4
4 | The delivery and installation of power line P FeZn 20x3mm SRPS N.B4.901 Č for the reception system and the down lead of the lightning conductor installation. |  | met. | 62
5 | Delivery and installation of the cross run for flat wires SRPS N.B4.936. |  | pcs. | 20
6 | Delivery and installation of the mechanical protection of the earth connection A 40×40×5 1500 SRPS N.B4.913 P. |  | pcs. | 4
7 | Delivery and installation of the cross run as a measurement connection SRPS N.B4.936. |  | pcs. | 4
8 | Delivery of materials and forming of lightning conductor bridge from the clamp to the horizontal sheet metal gutter spout, Fe-Zn 20x3mm ribbon, complete with connections and delivery and installation of spout terminal P SRPS N.B4.908. |  | pcs. | 4
9 | Delivery and installation of roof-conductor brackets for tile roof coverings SRPS N.B4.922 P. |  | pcs. | 32
10 | Delivery and installation of brackets for fixing roof ridge SRPS N.B4.920 P. |  | pcs. | 15
11 | Delivery and installation of brackets for brick walls B 100 SRPS N.B4.925 P. |  | pcs. | 10
12 | Reception-finishing works,costs of material procurement and transport. |  | lump sum
13 | Inspection and examination of earthing and lightning conductor installations. Measurement of earthing resistance at all measurement points of the existent lightning conductor installations. Examination of continuity. Issuing of expert finding - certificate of an authorised institution. |  | lump sum
TOTAL - II LIGHTNING INSTALLATIONS
ELECTRICAL INSTALLATIONS
Item number | DESCRIPTION OF WORKS | Unit of measurement | Unit of measurement | Quantity | Unit price in RSD | Total RSD
Deliver all required materials and build internal electrical installations fully in accordance with the effective SRPS regulations, enclosed graphical documentation, technical explanation and conditions, this bill of quantities and price calculation, with all required materials and competent workforce.
Items given below include, in addition to procurement of the overall materials, their transport to the construction site, storing, bringing to the place of installation, repair of all damaged parts, that is, restoring their original condition, with cleaning and disposal of debris to the landfill and correction of all technical and aesthetic mistakes made in installation.
POWER SUPPLY AND DISTRIBUTION CABINET
1.1. | Delivering, laying and connecting power supply cable from OMM to GRO. The connection is achieved with the cable N2 XH J 5x10. The calculation is done per metre of length of the laid cable, with all materials and tools required for placing.
|  |  | m' | 10
DISTRIBUTION CABINETS GRB
The equipment should be that made by a renowned supplier (Schneider-Electric or other suitable manufacturer) while the cabinet should be that of Evrotehna of other suitable type. Before it is made, the cabinet should be approved by the Supervisor.
1.2. | GRB
Delivery, mounting and installing switch cabinet for indoor installation into wall with IP 44 protection. The cabinet size should be determined depending on the equipment to be installed in it with 30% of free reserve space available. Three-line 3x12.
The following equipment should be installed in the cabinet:
| - four-pole faulty current protection switch FID 40/0,3 A |  | pcs. | 1
| - one-pole automatic switch 16 A "C", 6kA |  | pcs. | 18
| - one-pole automatic switch 10 A "C", 6kA |  | pcs. | 4
| - one-pole automatic switch 6 A "C", 6kA |  | pcs. | 1
| - faulty current protection switch 16/0.03 A |  | pcs. | 1
| reserve 10A |  | pcs. | 3
| reserve 16A |  | pcs. | 3
- reserved mounting place 20%
| - small and non-specified materials N,PE, connection clamps, glands, cable channels, marking stickers, cables for internal connections, etc. |  | lump sum | 1
| TOTAL FOR GRB |  | pcs. | 1
1.3 | OIP metal cabinet,
with copper bus 15x3
with brass bolts M8.
| OIP set |  | set | 1
INSTALLATIONS
Installation of electrical lighting and sockets is performed with halogen-free cables with a required number of wires and cross section, with the rated voltage of 0.66 kV. Used for the electrical lighting installation are the cables with the cross section of 1.5 mm2, while those with the cross section of 2.5 mm2 are used for installation of sockets.
1.4. | Delivery and laying of cable N2XH J (2,3-5)x1.5 mm2 for installation of regular, alternating and fan outlets, lighting point. The cable is chased into the wall, under plaster. Complete cable with IP20 distribution boxes and connections in those.
| cable N2 XH J 2x1.5 |  | m | 30
| cable N2 XH J 3x1.5 |  | m | 270
| cable N2 XH J 5x1.5 |  | m | 30
1.5 | Delivery and placing of cable N2XH J 3x2.5 mm2 for single-phase Schuko socket and fixed outlets. The cable is chased into the wall, under plaster. Complete cable with IP20 distribution boxes and connections in those.
| cable N2 XH J 3x2.5 |  | m | 350
1.6 | Laying cables for earthing of metal masses in the facility and sanitary premises. Laid in a 11 mm pipe, in the part from potential equalisation or from the panel to the potential equalisation box is the protective conductor P-Y 1x6 mm2, while the protective conductor of P-Y 1x4 mm is laid into a pipe with 11 mm diameter is laid from the potential equalisation box to the very metal masses. Complete cable with pipes. Average length of 15 m.
|  |  | pcs. | 2
INSTALLATION MATERIAL
The installation material and tools should be mounted and connected at indicated places. All switches of general lighting should be placed at the height h = 1.5 m from the floor. All sockets of general purpose should be placed at the height h = 0.4 m. Technological sockets should be placed at the indicated height. All switches and sockets comply with the SRPS standard, are of modular type, Aling Conel or of other suitable type. Approval of the interior supervisor should be sought when choosing the mask type and colour.
1.7 | - One-pole switch 230 V, 10A, 2M-MODE, with IP20 protection, with a box for installation into the wall, with the mask and colour according to the interior designer’s choice
|  |  | pcs. | 7
1.8 | - One-pole switch 230 V, 10A, 2M-MODE, with IP20 protection, with a box for installation into the wall, with power on indicator, with the mask and colour according to the interior designer’s choice
|  |  | pcs. | 4
1.9 | - Serial switch 230 V, 10A, 2M-MODE, with IP20 protection, with a box for installation into the wall, with the mask and colour according to the interior designer’s choice
|  |  | pcs. | 1
1.10 | - Dimmer unit set. Dimmer for DALI rail of Philips UID8620/00 DALI Dimmer type or other suitable type
|  |  | pcs. | 2
1.11 | Single-phase socket with protective contact 230 V, 16A with IP55 protection with M2 box for installation into the wall, with the mask and colour according to interior designer’s choice
|  |  | pcs. | 8
1.12 | Set of 1 single-phase Schuko socket and protection from direct contact with protective contact 230 V, 16 A, with IP 20 protection with M2 box for installation into the wall, with the mask and colour according to interior designer’s choice.
|  |  | pcs. | 7
1.13 | Set of 1 single-phase Schuko socket and 1 x RCA and protection from direct contact with protective contact 230 V, 16 A, with IP 20 protection with M3 box for installation into the wall, with the mask and colour according to interior designer’s choice.
|  |  | pcs. | 2
1.14 | Set of 2 single-phase Schuko sockets and protection from direct contact with protective contact 230 V, 16 A, with IP 20 protection with M4 box for installation into the wall, with the mask and colour according to interior designer’s choice.
|  |  | pcs. | 10
1.15 | Set of 2 single-phase Schuko sockets and 2 of Euro-standard type and protection from direct contact with protective contact 230 V, 16 A, with IP 20 protection with M7 box for installation into the wall, with the mask and colour according to interior designer’s choice.
|  |  | pcs. | 3
1.16 | Potential equalising box for installation in sanitary block.
|  |  | pcs. | 1
LIGHTS
Delivery, installation and electrical connections of bulb holders of the given light type with own power supply source (anti-panic lights) as well as all additional materials required for installation. Set of lights with LED light source of relevant rating and type.
1.17 | Type S1. Surface-mounted lamp set
Surface-mounted wide angle (135 degrees) LED lamp of downlighter type, envisaged for mounting on the ceiling for hallway lighting. Degree of mechanical protection is IP20, and impact resistance is IK02, while the rating class is I. The lamp is delivered completed with LED modules of the light colour 4000K, electronically pre-connected devices and colour reproduction index of Ra80. Efficiency min. 71lm/W, system initial flux 2000lm. Period within which the light flux drops to 90% of the initial flux is 15,000 hours, while the period for drop to 80% level is 30,000 hours. Maximum 1.5% of drivers will be faulty after 5,000 hours. Lampe temperature range is form 0 to +35 degrees of Celsius. The lamp should comply with the European directives pertaining to relevant products and have a CE mark. The lamp is Philips CoreLine SlimDownlight DN135C LED20S/840 PSU II WH.28W or of other suitable type
|  |  | pcs. | 5
1.18 | Type S2. Built-in lamp set
A wide-angle LED lamp designed for mounting in lowered monolithic or Amstrong ceiling with 216mm outer diameter and a cutting diameter of 200mm, with maximum depth of 95mm. The lamp housing is made of aluminium, painted in RAL9010 white colour, while the polycarbonate aluminium lamp reflector and the optic block made of polycarbonate. Mechanical protection degree is IP20, and impact resistance is IK02, and the current rating is II. The lamp is delivered complete with LED modules of the light colour 4000K, electronically pre-connected devices and colour reproduction index of Ra80. Total system flux is 2200lm, while maximum rating of the system is 24W. The period required for the light flux to drop to 90% of the initial flux is 25,000 hours, while the period required for a drop to 80% is 50,000 hours.The lamp should comply with the European standard for safe and proper operation, and have an ENEC mark. The lamp should comply with the European directives pertaining to relevant products and have a CE mark. The lamp is of Philips CoreLine GreenSpace DN470B LED20S/840 PSE-E WH type. 24W or suitable type
|  |  | pcs. | 19
1.19 | Type S3. Surface-mounted lamp similar to type
The surface-mounted lamp is made in LED technology, envisaged for mounting on the ceiling, with dimensions 20x120mm, for lighting indoor premises. The lamp housing and reflector are made of steel while the optical part is made of polycarbonate, with linear LED diodes. The lamp is in white colour. Degree of mechanical protection is IP20, and impact resistance is IK02, while the rating class is I. The lamp is delivered completed with LED modules of the light colour 4000K, electronically pre-connected DALI devices and colour reproduction index of Ra80. Efficiency min. 110lm/W, total system flux 3400lm. Total power of the system is 31W. Period within which the light flux drops to 90% of the initial flux is 15,000 hours, while the period for drop to 80% level is 30,000 hours. Maximum 1% of drivers will be faulty after 5,000 hours. Lamp temperature range is form +10 to +40 degrees of Celsius.
The lamp is dimmable and it may be dimmed down to 1% of light flux. The lamp may be mounted with movement sensor and the sensor for measurement of light volume. The lamp should comply with European standard for safe and correct operation and have an ENEC mark. The lamp should comply with the European directives pertaining to relevant products and have a CE mark. The lamp is of Philips CoreLine Surface SM120V LED37S/840 PSU W20L120.31W type, or other suitable type
|  |  | pcs. | 2
1.20 | Type S4. Surface-mounted lamp similar to type
The surface-mounted lamp is made in LED technology, envisaged for mounting on the ceiling, with dimensions 20x120mm, for lighting indoor premises. The lamp housing and reflector are made of steel while the optical part is made of polycarbonate, with linear LED diodes. The lamp is in white colour. Degree of mechanical protection is IP20, and impact resistance is IK02, while the rating class is I. The lamp is delivered completed with LED modules of the light colour 4000K, electronically pre-connected devices and colour reproduction index of Ra80. Efficiency min. 91lm/W, total system flux 3700lm. Total power of the system is 40.5W. Period within which the light flux drops to 90% of the initial flux is 15,000 hours, while the period for drop to 80% level is 30,000 hours. Maximum 1% of drivers will be faulty after 5,000 hours. Lamp temperature range is form +10 to +40 degrees of Celsius. The lamp’s mass is 3.4 kg. The lamp may be mounted with movement sensor and the sensor for measurement of light volume. The lamp should comply with the European directives pertaining to relevant products and have a CE mark. The lamp is of Philips CoreLine Surface SM120V LED37S/840 PSU W20L120 40.5W type, or other suitable type
|  |  | pcs. | 2
1.21 | Type S5. Rail projector set similar to type
Rail wide angle LED lamp of projector type, envisaged for mounting on DALI rail for exhibition lighting. The lamp’s turning radius is 350 degrees, while the optical part may turn up to 90 degrees. The lamp housing is made of aluminium, while the housing of the control gear part is made of plastic. The lamp is in white colour. The lamp is delivered complete with LED modules of the light colour 4000K, with DALI electronically pre-connection devices and colour reproduction index of Ra90. Total system flux is 2700lm. Maximum power of the system is 25W. The mass of the lamp is 1.2, period required for the light flux to drops to 90% of the initial flux is 25,000 hours, while the period required for drop to 80% level is 50,000 hours. Maximum 1% of drivers will be faulty after 5,000 hours. Lampe temperature range is form 0 to +35 degrees of Celsius. The lamp should comply with European standard for safe and correct operation and have an ENEC mark. The lamp should comply with the European directives pertaining to relevant products and have a CE mark. The lamp is of Philips StyliD ST740T LED27S/840 PSED WB WH type or other suitable type
|  |  | pcs. | 7
1.22 | Type S6. Surface-mounted lamp similar to type
Surface-mounted LED lamp envisaged to be mounted on the ceiling/wall of circular shape, with diameter of 344mm, for lighting of sanitary blocks. The lamp housing is made of polycarbonate, painted white. Degree of mechanical protection is IP65, and impact resistance is IK10, while the rating class is I. The lamp is delivered completed with LED modules of the light colour 4000K, dimmable electronically pre-connected devices and colour reproduction index of Ra80. Efficiency min. 67lm/W, total system flux 1200lm. Maximum power of the system is 18W. Period required for the light flux to drop to 90% of the initial flux is 15,000 hours, while the period required for a drop to 80% level is 30,000 hours. The lamp should comply with the European directives pertaining to relevant products and have a CE mark. The lamp is of Philips CoreLine WL120V LED12S/840 PSR WH.18W type, or other suitable type
|  |  | pcs. | 6
1.23 | Type S7. Surface-mounted lamp similar to type
GONDOLA IP65 CorePro Led bulb 9W E-27 or other suitable type
|  |  | pcs. | 2
1.24 | Type S8, anti-panic lamp LED 6W, 230 V, with own power source (batteries with 2h operation autonomy), IP20.
|  |  | pcs. | 4
1.25 | Type S9. Surface-mounted lamp similar to type
Surface-mounted, watertight, wide-angle LED lamp with rounded edges, envisaged for mounting on ceiling, dimensions 1223x87mm, for lighting of technical premises. The housing light is made of polycarbonate, coloured grey, as well as the optical block and protector. Degree of mechanical protection is IP65, and impact resistance is IK08, while the rating class is I. The lamp is delivered completed with LED modules of the light colour 4000K, electronically pre-connected devices and colour reproduction index of Ra80. Efficiency min. 105lm/W, total system flux 4000lm. Maximum power of the system is 38W. The period required for the light flux to drop to 90% of the initial flux is 15,000 hours, while the period required for a drop to 80% is 30,000 hours.The lamp should comply with the European standard for safe and proper operation, and have an ENEC mark. The lamp should comply with the European directives pertaining to relevant products and have a CE mark. The lamp is of Philips CoreLine Waterproof WT120C LED40S/840 PSU L1200 type. 38W, or other suitable type
|  |  | pcs. | 1
1.26 | Type S10. Projector rails set similar to type
DALI rail of RCS750 type produced by Philips, or other suitable type, complete with all required power supply, clamps and connectors for mounting 2x8m
|  |  | set | 1
INSTALLATION PIPES
1.27 | Delivery and laying of PVC halogen-free pipes during construction works
for indoor installation according to distribution requirements.
- fi 16, 23, 32 mm
|  |  | m' | 40
1.28 | Accompanying installation material and works.
| set |  | pcs. | 1
FINISHING WORKS AND TESTING OF HIGH VOLTAGE INSTALLATIONS
1.29 | Upon the completion of works on electrical installations the Contractor is obliged to do the following:
- Enclose all required certificates for the installed equipment to the Investor
- Carry out an inspection and functional testing of electrical installations as regards insulation and safety from too high touch voltage. Carry out measurements of earthing resistance and loop resistance for defects and deliver the obtained results to the Investor
- Remove potential technical and aesthetic faults
- Enter all changes in the course of performance of electrical works in one copy and in digital form on a CD
- Handover of installations for use by the Investor.
|  |  | set | 1
TOTAL FOR ELECTRICAL INSTALLATIONS
ANTI-BURGLARY SYSTEM
1 | Central unit for anti-burglary protection, at least 2 partitions, addressable type, along with batteries, transformer unit and protective box. Type: Paradox EVO192 or suitable |  |  | 1
2 | Keypad, LCD display Type: Paradox K641+ |  | pcs. | 2
3 | Communication module for connection to phone line for remote informing on the system condition and system management (remote activation and deactivation of the system) Type: Paradox VDMP3 or suitable |  | pcs. | 1
4 | GSM module for communication via GSM network Type: Paradox PCS250 or suitable |  | pcs. | 1
5 | IP module for communication and control of system via local computer network and/or internet (TCP/IP protocol) Type: Paradox IP150 |  | pcs. | 1
6 | Passive infrared movement detector, quad detection, addressable, complete with carrier Type: Paradox DM60 or suitable |  | pcs. | 8
7 | External siren, double-protection, 120dB, complete with its battery 12V, 7Ah Type: SIR/ PL or suitable |  | pcs. | 1
8 | Connecting and mounting all elements of the anti-burglary protection system, central unit configuration, installation examining, system commissioning and training of users |  | set | 1
Total for ANTI-BURGLARY INSTALLATIONS
SUMMARY
1 | I ELECTRICAL INSTALLATIONS
2 | II LIGHTNING INSTALLATIONS
3 | ELECTRICAL INSTALLATIONS
4 | ANTI-BURGLARY SYSTEM
TOTAL TECHNICAL BUILDING :

## 4.Overall el.works
4 - ELECTRICAL INSTALLATIONS PROJECT - KLEK
OVERALL SUMMARY-ELECTRICAL WORKS
I | POWER CABLES AND OUTDOOR LIGHTING
II | TECHNICAL BUILDING
TOTAL ELECTRICAL INSTALLATIONS PROJECT - KLEK (RSD)

## 6.1.Mech.works - lock
PRICE CALCULATION FOR KLEK SHIP LOCK
MECHANICAL WORKS
No. | Description | Unit of measure | Quantity | JCM | Јед. Цена | JCR | Material(price without VAT) | Work (price without VAT) | Total (price without VAT)
I UPPER DOOR
1. | Upper door leaf - repair
The inspection of the parts of the door construction positioned above the wall, established that the steel gate plate (lining) and the supporting structure corroded only partially and, based on the estimation of the state of a part of the construction, it is possible to repair the door without making a new one.
| • Anti-corrosion protection of the gate plate and supporting construction door leaf. Price given per kg of protected surface. | kg | 5350
| • Repair the gate plate and supporting construction door leaf. Price has to calculate all necessary work and material. Price given per kg of new mounted material. | kg | 1200
| • Replacement of wooden sealing beams (oak), cutting, impregnation, drilling of openings for bolts. | m3 | 0.5 | 76700 |  | 76700
| • Procurement and installation of wooden gasket | kg | 75
TOTAL:
• Other (bolts, nuts, washers,...) Procurement and installation.
TOTAL_ UPPER DOOR LEAF:
2. | Upper bearing
| • Upper bearing set, cutting, drilling, installation | kg | 150 | 1183.7 | 0 | 591.85
Upper bearing pillar
Corner plate for connection with pillar
Brace hinges
Upper bearing braces
Door axis hinge
Bearing pins
TOTAL:
• Other (preparation, installation and concreting of the upper bearing pillars, bolts, nuts, washers, ...)
TOTAL_UPPER BEARING:
3. | Lower bearing
| • Lower bearing base | kg | 120 | 1775.55 | 0 | 236.74
| • Flanges | kg | 110 | 1657.18 |  | 236.74
| • Shaft | kg | 20 | 1775.55 |  | 295.925
| • Tyre | pcs. | 1 | 6983.83 |  | 0
| • Calotte | kg | 15 | 946.96 |  | 414.295
| • Lower bearing extension | kg | 30 | 828.59 |  | 177.555
| • Flange | kg | 15 | 591.85 |  | 177.555
| • Anchor | kg | 10 | 118.37 |  | 118.37
TOTAL:
• Other (preparation, installation and concreting of the lower bearing pillars, cylindric pins, bolts, nuts, washers, ...)
TOTAL LOWER BEARING:
4. | Door opening/closing device
| • Repair of the supporting structure of the device | kg | 400
| • Inspection, cleaning and lubrication of the transmission (gears, shafts, bearings, levers, …) | kg | 200
| • Rack and pinion making | kg | 100
• Other (wedges, split pins, axles, greasers, bolts, nuts, washers, …)
TOTAL FOR DOOR OPENING/CLOSING DEVICE:
5. | Fence and pedestrian pathway on upper door
| • Pathway supporting structure | kg | 200 | 82.859 | 0 | 142.044
| • Fence construction (handrail pillars) | kg | 70 | 82.859 |  | 142.044
| • Tread (ribbed sheet metal) | m2 | 3.5 | 3551.1 |  | 2367.4
TOTAL:
• Other (rivets, bolts, nuts, washers, …)
TOTAL FOR FENCE AND PED. PATHWAY ON UPPER DOOR:
6. | Mechanical equipment in the tunnel/canal
| • Repair od the supporting structure (metal profiles, construction of the flashboard raising mechanism, rack and pinion guides, …) | kg | 350
| • Inspection, cleaning and lubrication of transmission and counterbalance (gears, shafts, bearings, chain wheels, levers, …), potential replacement of worn-out elements | kg | 250
• Flashboard making
• Chain, 2 pcs
• Other (wedges, split pins, axles, elastic pins, bolts, nuts, washers, …)
TOTAL FOR CIRCULATING CANAL:
| TOTAL FOR SHIP LOCK UPPER DOOR | [7 empty] | 0
| 1. Upper door leaf | pcs. | 2 | [5 empty] | 0
2. Demounting, mounting, examining and trial operation
3. Other (transport, insurance ...)
TOTAL FOR UPPER DOOR:
II MIDDLE DOOR
1. | Middle door leaf - construction of new door leaf
| •Gate plate, ≠8 х 5570 х 5620, riveting, welding and anti-corrosion protection | kg | 2000 | 71.022 | 0 | 142.044
| • Supporting structure, cutting, welding and anti-corrosion protection |  | 3600 | 82.859 |  | 82.859
| •Wooden gasket (oak), cutting, impregnation, drilling | m3 | 0.75 | 76940.5 |  | 76940.5
| •Rubber gasket | kg | 50 | 0 |  | 0
| • Rivets | pcs. | 900 | 118.37 |  | 118.37
TOTAL:
•Other (bolts, nuts, washers, ...)
TOTAL_MIDDLE DOOR LEAF:
2. | Upper bearing
| • Upper bearing set, cutting, drilling, installation | kg | 150 | 1183.7 | 0 | 591.85
Upper bearing pillar
Corner plate for connection with pillar
Brace hinges
Upper bearing braces
Door axis hinge
Bearing pins
TOTAL:
• Other (preparation, installation and concreting of the upper bearing pillars, bolts, nuts, washers, ...)
TOTAL_UPPER BEARING:
3. | Lower bearing
| • Lower bearing base | kg | 120 | 1775.55 | 0 | 236.74
| • Flanges | kg | 110 | 1657.18 |  | 236.74
| • Shaft | kg | 20 | 1775.55 |  | 295.925
| • Tyre | pcs. | 1 | 6983.83 |  | 0
| • Calotte | kg | 15 | 946.96 |  | 414.295
| • Lower bearing extension | kg | 30 | 828.59 |  | 177.555
| • Flange | kg | 15 | 591.85 |  | 177.555
| • Anchor | kg | 10 | 118.37 |  | 118.37
TOTAL:
• Other (preparation, installation and concreting of the lower bearing pillars, cylindric pins, bolts, nuts, washers, ...)
TOTAL LOWER BEARING:
4. | Door opening/closing device
| • Repair of the supporting structure of the device | kg | 400
| • Inspection, cleaning and lubrication of the transmission (gears, shafts, bearings, levers, …) | kg | 200
| • Rack and pinion making | kg | 100
• Other (wedges, split pins, axles, greasers, bolts, nuts, washers, …)
TOTAL FOR DOOR OPENING/CLOSING DEVICE:
5. | Device for middle door flashboard lifting
| • Repair of the supporting structure and counterbalance | kg | 300
• Inspection, cleaning and lubrication of the transmission (gears, chain wheels - 2 pcs., chains - 2 pcs., bearings, shafts…)
• Other (wedges, split pins, axles, elastic pins, bolts, nuts, washers …)
TOTAL FOR MIDDLE DOOR FLASHBOARD LIFTING:
6. | Middle door flashboard
| • Bearing lever | kg | 105 | 106.533 | 0 | 71.022
| • Wooden plate (oak boards), (processing, protection and installation) | m3 | 0.15 | 76940.5 |  | 76940.5
| • Wooden carrier (oak), (processing, drilling of holes, protection) | m3 | 0.02 | 0 |  | 0
| • Frame tie plate (cutting and anti-corrosion protection) | kg | 100 | 82.859 |  | 71.022
| • Metal frame, (cutting, drilling of openings and anti-corrosion protection) | kg | 50 | 0 |  | 0
| • Rubber gasket | kg | 3 | 0 |  | 0
| • Press sheet, (cutting, drilling, anti-corrosion protection) | kg | 10 | 82.859 |  | 142.044
TOTAL:
• Other (bolts, nuts, washers, ...)
TOTAL FOR MIDDLE DOOR FLASHBOARD:
7. | Fence and pedestrian pathway on middle door
| • Pathway supporting structure | kg | 140 | 82.859 | 0 | 142.044
| • Fence construction (handrail pillars) | kg | 70 | 82.859 |  | 142.044
| • Tread (ribbed sheet metal) | m2 | 3.5 | 3551.1 |  | 2367.4
TOTAL:
• Other (rivets, bolts, nuts, washers, …)
TOTAL FOR FENCE AND PED. PATHWAY ON MIDDLE DOOR:
8. | Mechanical equipment in the tunnel/canal
| • Repair od the supporting structure (metal profiles, construction of the flashboard raising mechanism, rack and pinion guides, …) | kg | 350
| • Inspection, cleaning and lubrication of transmission and counterbalance (gears, shafts, bearings, chain wheels, levers, …), potential replacement of worn-out elements | kg | 250
• Flashboard making
• Chain, 2 pcs
• Other (wedges, split pins, axles, elastic pins, bolts, nuts, washers, …)
TOTAL FOR CIRCULATING CANAL:
TOTAL FOR SHIP LOCK MIDDLE DOOR
| 1. Middle door leaf | pcs. | 2
2. Demounting, mounting, examining and trial operation
3. Other (transport, insurance ...)
TOTAL FOR MIDDLE DOOR:
III LOWER DOOR
1. | Lower door leaf - demounting
Since lower door is not to be used in the future , it is necessary to demount door leaf and the associated equipment and place it at appropriate location near the lock.
| • Demounting door leaf and the associated equipment and placing it at appropriate location near the lock. | kg | 6000
TOTAL_LOWER DOOR LEAF:
TOTAL FOR SHIP LOCK LOWER DOOR
| 1. Lower door leaf | pcs. | 2 | [5 empty] | 0
2. Other (transport,preparatory works, material, insurance ...)
TOTAL FOR LOWER DOOR:
IV STOP LOGS
| • Gate plate, ≠8 х 4170 х 5450, riveting, welding and anti-corrosion protection | kg | 1200 | 71.022 | 0 | 142.044
| • Supporting structure (profiles, board material, …), cutting, welding and anti-corrosion protection | kg | 2100 | 82.859 |  | 142.044
| • Stop log spring ≠15 х 120 х 805, 2 pcs. | kg | 10 | 1420.44 |  | 2367.4
| • Rubber gasket | kg | 38
TOTAL FOR STOP LOG:
TOTAL_ALL STOP LOGS
| 1. Stop log | pcs. | 11 | [5 empty] | 0
2. Other (bolts, nuts, washers, transport, insurance, ...)
TOTAL FOR STOP LOGS:
TOTAL_KLEK SHIP LOCK:

## 6.2.Mech.works-floodgate
PRICE CALCULATION FOR KLEK FLOODGATE
MECHANICAL WORKS
No. | Description | Unit of measure | Quantity | JCM | Јед. Цена | JCR | Material(price without VAT) | Work (price without VAT) | Total (price without VAT)
1. | Frames, 17 pieces
| • Inspection and overhaul of the supporting structure of frames and rivets, cleaning and anti-corrosion protection | kg | 24000
• Other (repair of elements for connecting frames with support, elements for crane pathway connection to frame, ...)
| TOTAL_ALL FRAMES: | pcs. | 17
2. | Lateral frame
| • Inspection and overhaul of the lateral frame supporting structure, repair and anti-corrosion protection | kg | 600
• Other (raising and returning into water - installation, ...)
TOTAL_LATERAL FRAME:
3. | Flashboards, 20 pcs
| • Wooden gaskets (boards), ~ 6 pcs | m3 | 0.085 | 76940.5 |  | 76940.5
| • Profiles for connecting wooden gaskets, L100 x 75 x 9, L=1050 mm, 4 pcs., | kg | 50 | 82.859 |  | 82.859
| • Sheet metal for eye connection, ≠10 х 60 х 930, 2 pieces | kg | 10 | 82.859 |  | 82.859
| • Eye | kg | 2 | 118.37 |  | 118.37
TOTAL:
• Other (preparation, installation, bolts, nuts, washers, ...) 15% (of the total price)
TOTAL_FLASHBOARD:
| TOTAL_ALL FLASHBOARDS: | pcs. | 20
4. | Mechanism/winch for raising of frames
| • Chain for raising/lowering of frames, welded chain (with links), (d x t) 23 x 64, 1 pc | m | 221
| • Repair of metal casing (cleaning, painting, …) | kg | 1700
• Inspection and repair of elements for moment transfer from the lever to drive wheel chain (gears, shafts, wedges, bearings, wheel chain, …). Potential replacement of worn-out elements.
• Other (potential replacement and repair of elements of threaded joints, chain casing, …)
| TOTAL_ MECHANISM FOR FRAME RAISING: | [5 empty] | 0 | 0
5. | Crane trolley and transport trolley rails
| • Defect diagnosis and overhaul of rails above the floodgate (on frames) | kg | 900
| • Defect diagnosis and overhaul of rails outside the floodgate and in the warehouse | kg | 2970
• Other (connection elements/plates, bolts, nuts, washers, …)
| TOTAL_RAILS: | [5 empty] | 0 | 0
6. | Crane for mounting/demounting flashboards
| Inspection and anti-corrosion protection of the crane supporting structure | kg | 350
• Inspection, repair, and protection of the wheel and transmission mechanisms (gears, drum, rope sheave, rope)
| • Crossbeam making | kg | 35
• Crane trolley
| Inspection and anti-corrosion protection of the trolley supporting structure | kg | 340
| Inspection, cleaning and potential replacement of shafts, wheels and bearings | kg | 450
| Cleaning and protection of treads (ribbed sheet metal) | m2 | 4.2
• Other (levers, rivets, bolts, nuts, washers, …)
| TOTAL_CRANE FOR FLASHBOARDS: | [5 empty] | 0 | 0
7. | Trolley for transport of flashboards, 2 pcs
| • Inspection and anti-corrosion protection of the trolley supporting structure | kg | 90
| • Inspection, cleaning and potential replacement of shafts, wheels and bearings | kg | 375
| • Cleaning and protection of treads (ribbed sheet metal) | m2 | 3
TOTAL:
• Other (rivets, bolts, nuts, washers, …)
| TOTAL_ALL FLASHBOARD TROLLEYS: | pcs. | 2
8. | Swivelling platform above lateral frame
| • Repair of the platform supporting structure, anti-corrosion protection | kg | 700
| • Inspection and replacement of worn-out parts within the lever for platform rotation | kg | 45
| • Cleaning and protection of treads (ribbed sheet metal) | m2 | 9.5
| TOTAL_SWIVELLING PLATFORM: | [5 empty] | 0 | 0
9. | Tread over the floodgate and protective fence
| • Tread repair (ribbed sheet metal) | m2 | 50
| • Fence repair | kg | 510
| TOTAL_TREAD AND FENCE: | [5 empty] | 0 | 0
10. | Auxiliary device for mounting/demounting flashboards
| • Overhaul of the device supporting structure, anti-corrosion protection | kg | 120
| • Defect diagnosis for device transmission (gears, shafts, lever, drum, …) and potential replacement of worn-out parts | kg | 200
| • Steel rope, Ф10 | m | 20
| TOTAL_AUXILIARY DEVICES: | [5 empty] | 0 | 0
1. Demounting, mounting, examining and trial operation
2. Other (transport, insurance ...)
TOTAL_FLOODGATE

## 6.3.Mech.works-warehouse crane
PRICE CALCULATION FOR WAREHOUSE BRIDGE CRANE - KLEK
MECHANICAL WORKS
No. | Description | Unit of measure | Quantity | JCM | Јед. Цена | JCR | Material(price without VAT) | Work (price without VAT) | Total (price without VAT)
1. | Bridge warehouse crane
| • Repair of construction of bridge crane (main carrier, lateral carriers, crane wheels, wheel chain for crane bridge drive, drive shaft, elements for connection of the main carrier with lateral carriers, …), anti-corrosion protection | kg | 700
| • Procurement of crane trolley and lift drive | pcs. | 1
| • Procurement of chains of crane bridge drive | m | 10
| • Procurement of chains of crane trolley drive | m | 10
| • Procurement of chains of lift drive | m | 8
TOTAL:
1. Demounting, mounting, examining and trial operation
2. Other (transport, insurance ...)
TOTAL BRIDGE CRANE:

## 6.Overall mech.works
OVERALL SUMMARY-MECHANICAL WORKS
I | KLEK CANAL LOCK
II | FLOODGATE
III | WAREHOUSE CRANE
TOTAL (RSD)

## Works-total
SUMMARY OF FACILITY WORKS - KLEK:
1 | ARCHITECTURAL WORKS ON TECHNICAL BUILDING |  | #REF!
2 | CONSTRUCTION WORKS ON THE SHIP LOCK |  | #REF!
3 | ELECTRICAL WORKS |  | #REF!
4 | MECHANICAL WORKS |  | #REF!
5 | THE DESIGN OF THE CONSTRUCTED FACILITY
6 | PLAN ON PREVENTIVE ACTIVITIES
Note 1:
THE DESIGN OF THE CONSTRUCTED FACILITY should include all facilities and works on which the works have been performed.
Note 2:
The PLAN ON PREVENTIVE ACTIVITIES should be created in accordance with the Regulation on Health and Safety on Construction Sites ("Official Gazette of RS", No. 14/2009 and 95/2010)
| WORKS, TOTAL: |  | #REF!
PRICES ARE WITHOUT VAT
Novi Sad, November 2018
Prepared by:
Jelena Solaković, B.Sc.C.E.