# ANNEX II + III :	 TECHNICAL SPECIFICATIONS + TECHNICAL OFFER

- Contract title : SCADA System	p 1 /…

Publication reference : 451/DUMBRAVITA/08

Columns 1-2 should be completed by the Contracting Authority

Columns 3-4 should be completed by the tenderer

Column 5 is reserved for the evaluation committee

Annex III - the Contractor's technical offer

The tenderers are requested to complete the template on the next pages:

- Column 2 is completed by the Contracting Authority shows the required specifications (not to be modified by the tenderer),

- Column 3 is to be filled in by the tenderer and must detail what is offered (for example the words “compliant” or “yes” are not sufficient)

- Column 4 allows the tenderer to make comments on its proposed supply and to make eventual references to the documentation

The eventual documentation supplied should clearly indicate (highlight, mark) the models offered and the options included, if any, so that the evaluators can see the exact configuration. Offers that do not permit to identify precisely the models and the specifications may be rejected by the evaluation committee.

The offer must be clear enough to allow the evaluators to make an easy comparison between the requested specifications and the offered specifications.

When brand names / specifications /regulations / standards (e.g. SR EN, STAS, ISO XXX etc.) referring to or describing products of a given brand or origin are used in the technical specifications they are used in descriptive purposes only or should be interpreted as equivalent.

| 1. Item Number | 2. Specifications Required | 3. Specifications Offered | 4. Notes, remarks, ref to documentation | 5. Evaluation Committee’s notes |
| --- | --- | --- | --- | --- |
| 1 | Central server – 1 piece Minimum requirements: 2 x processor 2.10 Ghz 64 Gb RAM 2 x HDD 1 TB Operating system Wireless keyboard and mouse Warranty 24 months |  |  |  |
| 2 | LED monitor– 1 piece Minimum requirements: 21`, full HD, optimal resolution 1920 x 1080, 16: 9 image aspect, luminosity 250cd / m2, 5ms response time |  |  |  |
| 3 | UPS – 1 piece Minimum requirements: - power capacity 2400 W / 2000VA - batteries included 6 x 9Ah / 12V - average charging time 6-9 hours up to 90% - average operating time 33 minutes - 25% charge 14 minutes - 50% charge 8 minutes -75% charge 5.5 minutes - control panel - audible alarm Overload protection. Overvoltage protection. Lightning protection. Full discharge or battery overload protection. Automatic voltage regulator. |  |  |  |
| 4 | 2. Black and white printer - 1 pc Minimum requirements: - format A4, A5, B5, 10 x 15cm, 13 x 18cm - printing speed 8 ipm - 60 sheet paper supply |  |  |  |
| 5 | Industrial dual SIM router – 1 pc Minimum requirements: - Dual SIM redundancy for persistent 2G/3G/4G cellular network connections - Management and maintenance via Web/CLI/SMS/SNMP - Antenna number: 2 - Operating environment: 40 to +75°C/5 to 95% RH - Robust industrial design |  |  |  |
| 6 | SCADA software license, 1000 tags, installed on the server - 1 pc |  |  |  |
| 7 | SCADA dispecer – 1 pc Minimum orders: Main SPAs - 10 pcs: - On - off the pump; - Pump operation -YES / NO; - Current - sub current / supercurrent measurement - Water level; - PTC / DK pump type sensors - Warnings; - Working hours Individual Pumping stations - 40 pcs: - On - off the pump; - Pump operation -YES / NO; - Level; - - PTC / DK pump type sensors - Warnings; - Working hours; The logic implemented in SCADA must take into account the following command philosophy: • • Alarmed LL means reaching the minimum level in the pumping station. It is recommended to stop the pumps; • • LL and H at rest correspond to the normal operating state, when the pumping station is being filled; • • H alarmed means that wastewater has accumulated in the station and it is necessary to start the drain pumps. The start is made according to the control scheme based on the time program in the Controller (PLC) which selects the start of one of the pumps; |  |  |  |
|  | • • Alarmed HH, means that for various reasons the pumping station is still filling. It is considered a fault situation, and if the fault is not caused by the malfunction of the pump, the commissioning and the pump at rest at that time are ordered according to the program in the Controller / SCADA; • • in the event that the communication is interrupted, the pumps in the pumping stations will normally operate automatically controlled by the water levels in the pumping station. The following elements (devices) must be provided on the front of the TSP automation panel: • • yellow lamp for signaling communication error; • • red mushroom button for emergency stop; • • level indicator with 2 programmable contacts to stop the pumps if the system does not work with remote control or the controller is defective. The level indicator can be parameterized locally or remotely via the RS485 port. • In this way a double protection is ensured; • protection in case of minimum fault and maximum fault will be performed directly from the minimum fault and maximum fault sensor by means of relays that also transmit a signal to the Controller for integration in the SCADA application; • • 3-position selector, for the control of each pump within the pumping station: • "START" / "STOP" / "Controller" (if the selector is set to the start position the pump starts if all operating conditions are met and the pump is ready. The operating conditions are as follows: the contactor can be powered at 24Vac, we have no faults from the thermistor, minimum level, maximum level, mushroom button, phase sequence monitoring relay, flood sensor) in case the selector is in the "START" / "STOP" positions the PLC cannot give any pump start control. |  |  |  |
|  | • • each pump will be provided with a lock switch that can be locked with a padlock; • • the following fault signaling lamps shall also be provided: system fault lamp, maximum level fault lamp, minimum level fault lamp |  |  |  |
| 8 | SCADA monitoring client – 1 pc |  |  |  |
| 9 | GSm / GPRS / 3G / Radio communication board -1 pc |  |  |  |

Warranty and post-warranty conditions

• Minimum 24 months from commissioning;

• The supplier will provide service during the warranty period;

• The supplier undertakes by warranty to keep spare parts available for at least 10 years from the date of delivery;

The supplier must include a catalog / prospectus sheet that exemplifies the operation of the system.

• Training of user staff included, at the beneficiary's headquarters and technical support during the warranty period;

• Certificate of quality and guarantee / technical approval, according to the legislation in force.