# VOLUME 3

# TECHNICAL SPECIFICATIONS

1. OUTDOOR STREET LED LIGHTING

DESCRIPTION OF THE TECHNICAL CHARACTERISTICS OF THE REQUESTED TYPES OF LAMPS

- Aluminum housing, divided into two sections, optical with LED modules and second one with the driver so that they are thermally separated.

- Finishing: Color gray fine structure. Epoxy protection against UV and corrosion.

- Lenses are made of PMMA, high transmittance (more than 90%), resistant to high temperatures and UV rays.

- Degree of mechanical protection: minimum IP66 in accordance to SRPS EN 60598-1 or equivalent.

- Connection voltage 230VAC, 50Hz. Power factor minimum 0.97.

- LED modules must be an universal type in such a way that they match the characteristics (module dimensions and LED arrangement) of the following families: Fortimo Fast Flex G4 DA/PHILIPS or RLE/TRIDONIC or WU-M-541/VOSSLOH SCHWABE or equivalent.

- Maximum current 700mA.

- Color temperature 4000K (+/-10%), color rendering index CRI≥70.

- Lifetime: Modules: ≥100000h(L90B10), driver: ≥100000h.

- Lamps have protection against high temperature, overload, short circuit, additional overvoltage protection 10kV.

- Ambient operating temperature range: -20°C to +35°C.

- The lamp must have a declaration of compliance with European directives: LVD, Rohs, ErP.

- The lamp manufacturer must have the following ISO certificates: ISO9001, ISO50001.

- It must have a CE mark.

- The lamp must have the ability to be reprogrammed directly at the mounting location without wires.

- The lamp must be remotely controllable via the power cable from the power cabinet.

- The option of group control of lamps on the same power supply route, and also the remote control system and the communication protocol must be connected to the central control system without additional upgrades in the lamps themselves.

- The lamp must have the function of setting the output flux, constant flux during the lifetime (CLO), autonomous dimming.

- The lamp must have a built-in (programmed) autonomous dimming in the following steps:

• From the moment of they turn on until 11 p.m., the lamps work at 100% light flux

• From 11 p.m. to midnight, the lamps operate at 70% light flux

• From midnight to 4 a.m., the lamps work at 50% light flux

• From 04:00 a.m. to 05:00 a.m. the lamps work at 70% light flux

• From 05:00 a.m. until the moment of switching off, public lighting lamps operate at 100% luminous flux

MANDATORY TECHNICAL REQUIREMENTS FOR FUNCTIONAL - STREET LAMPS

- Mounting on arm ø42-60mm. The protector is made of flat transparent tempered glass, minimum IK08 in accordance to SRPS EN 62262 or 60068-2-75 or equivalent

TYPE1

LED lamps must meet the photometric conditions according to the standard SRPS EN 13201-2,,Road lighting-Part 2: Required characteristics'', or equivalent, for lighting class M5 for the following input parameters: the distance between the poles is 37m; W/km ≤ 702; arrangement of columns one-sided from the bottom side; street with two lanes 5m wide; light center height from road is7m; maintenance factor 0.80; arm length 0.5m, angle 10 degrees; the distance of the optical center of the lamp from the road is -1m; standard road surface R3, q0: 0.070

Picture has informative/ non obligatory character

TYPE2

LED lamps must meet the photometric conditions according to the standard SRPS EN 13201-2,,Road lighting-Part 2: Required characteristics'', or equivalent, for lighting class M4 for the following input parameters: the distance between the poles is 35m; W/km ≤ 1537; arrangement of columns one-sided from the bottom side; street with two lanes 6m wide; light center height from road is10m; maintenance factor 0.80; arm length 1m, angle 10 degrees; the distance of the optical center of the lamp from the road is 0.5m; standard road surface R3, q0: 0.070

Picture has informative/ non obligatory character

TYPE3

LED lamps must meet the photometric conditions according to the standard SRPS EN 13201-2,,,Road lighting-Part 2: Required characteristics'', or equivalent, for lighting class M3 for the following input parameters: the distance between the poles is 40m; W/km ≤ 1750; arrangement of columns one-sided from the bottom side; street with two lanes 7m wide; light center height from road is10m; maintenance factor 0.80; arm length 1.5m, angle 0 degrees; the distance of the optical center of the lamp from the road is -0.5m; standard road surface R3, q0: 0.070

Picture has informative/ non obligatory character

TYPE4

LED lamps must meet the photometric conditions according to the standard SRPS EN 13201-2,,,Road lighting-Part 2: Required characteristics'', or equivalent, for lighting class M2 for the following input parameters: the distance between the poles is 30m; W/km ≤ 3432; arrangement of columns one-sided from the bottom side; street with three lanes 10.5m wide; light center height from road is12m; maintenance factor 0.80; arm length 1.5m, angle 0 degrees; the distance of the optical center of the lamp from the road is 0m; standard road surface R3, q0: 0.070

Picture has informative/ non obligatory character

TYPE5

LED lamps must meet the photometric conditions according to the standard SRPS EN 13201-2,,,Road lighting-Part 2: Required characteristics'', or equivalent, for lighting class M1 for the following input parameters: the distance between the poles is 27m; W/km ≤ 6438; arrangement of columns one-sided from the bottom side; street with three lanes 10.5m wide; light center height from road is13m; maintenance factor 0.80; arm length 1.5m, angle 15 degrees; the distance of the optical center of the lamp from the road is 0.5m; standard road surface R3, q0: 0.070

Picture has informative/ non obligatory character

ARMS:

Universal steel support for lamps for all types of poles with a suitable clamp according to the type of pole. The dimensions and appearance of the lamp holder are given on picture. Lamp holders-arms should be protected against corrosion by hot galvanizing according to the SRPS EN ISO 1461 standard or equivalent. Note: Depending on the requirements in the calculation and the needs of the location, the angle of the arm varies from 0 to 15 degrees.

Pictures have informative/ non obligatory character

Mechanical protection - a protective covering similar to type F3- 100.3MM- L=2000 mm or corresponding certified according to SRPS EN 62262 or 60068-2-75 with a degree of impact resistance minimum IK08 or equivalent.

Fidos 1.5-10/16-95. The body is made of polyamide with glass fibers by injection molding, the contacts are made by stamping Cu sheet with extra hardness HB 110. The connecting element is a quality bag screw. It is used to connect the drain line, which has a cross-section of 1.5 to 10 mm2, and the supply line of 16-95 mm2. It is completely insulated and waterproof. It is most suitable for connecting lighting fixtures to the LV network. Certified in accordance with SRPS n f 4.101/86 or equivalent.

In order to prove the technical characteristics, i.e. compliance with the technical characteristics Contracting Authority will ask from from tenderer with acceptable offer and lowest compliant price to submit following before contract signature:

For lamps:

- One lamp sample that must fully match the technical characteristics of the offer. Along with the samples, deliver non-chargeable software to the Contracting Authority (on DVD/CD, USB or by providing a link) and a device for programming the lamps wirelessly with instructions, as well as a device for remote control via a power cable. It is mandatory to indicate on the box which types the sample refers to.

- Warranty stamped and signed by the lamp manufacturer/importer or equivalent.

- Catalogs of offered lamps and a technical sheet with a description confirming the fulfillment of each of the required technical parameters

- Technical sheet of the lens that confirms its material, transmittance and polar diagram, compatibility with the offered LED module.

- LED module technical sheet. With this technical sheet, the Contracting Authority must make sure that the LED source has the same characteristics as requested (width of the module, arrangement and distance between the LED’s, efficiency and flux to the reference current 700mA).

- Technical description of the remote control system. The minimum requirement and need of the Contracting Authority is that the lamps can be remotely reprogrammed in the form of changing the light scenes (dimming). In the description of the system, clearly indicate how management works, which protocol it uses and how it is systematically connected to the central management system. Prove the descriptions and claims through attachments in the form of technical sheets and instructions of the manufacturer of the device for remote programming of the system offered. Attach the technical sheets of the ballast devices in the lamps, the connection diagrams, as well as the technical sheets of the components that complement the system in the central control system.

- Technical data sheet of the driver device installed in the lamps so that the Contracting Authority can make sure of the required technical characteristics (efficiency, power factor, voltage range), possibilities, programmable options and lifetime.

- Certificate of an accredited laboratory for IP degree (in accordance with SRPS EN 60598-1 or equivalent) and IK protection (in accordance with SRPS EN 62262 or 60068-2-75 or equivalent).

- The declaration of conformity of the lamp manufacturer according to which the Contracting Authority can make sure with which directives it is in conformity (LVD, ErP, Rohs, or corresponding) and that it has a CE mark or corresponding.

- Valid ISO certificates (ISO9001,50001 or equivalent) of the manufacturer.

- Photometric report (in accordance with the LM-79 standard or equivalent) showing the polar diagram of the offered lamps, tables of light intensity and transmission efficiency (LOR) of the lamps.

For arm:

- A sample of arm that must fully match the technical characteristics of the offer.

- Certificate from an accredited laboratory that the supports are anti-corrosively protected by the method of hot galvanizing according to the SRPS EN ISO 1461 standard or equivalent.

- Warranty stamped and signed by the manufacturer.

For the external grounding cable:

- A sample of the external grounding cable, which must fully correspond to the technical characteristics of the offer.

- Certificate of an accredited laboratory in accordance with SRPS U.M1.047/1987 for a force of 10 kN or equivalent.

- Warranty stamped and signed by the manufacturer.

For the protective cover:

- A sample of the protective cover, which must fully correspond to the technical characteristics of the offer.

- Certificate of an accredited laboratory for the degree of IC protection in accordance with SRPS EN 62262 or 60068-2-75 or equivalent.

- Warranty stamped and signed by the manufacturer.

For fidos:

- A sample of fidos that must fully correspond to the technical characteristics of the offer.

- Certificate of an accredited laboratory in accordance with SRPS n f 4.101/86 or equivalent.

- Warranty stamped and signed by the manufacturer.

2. INDOOR LED LIGHTING TOWN HALL

Indoor light sources inside Town Hall will be replaced with energy efficient LED counterparts. Contractor is expected to replace light sources and also lamp if necessary. There are 3 types of lamps currently installed in Town Hall which need to be replaced. LED lights colour for all types of light sources should be in range 2700K-4000K, have lifetime at least 50.000 hours and in case that lamp is to be replaced it should have equivalent or better photometry characteristics than currently installed.

TYPE 1 INDOOR

Replacement of 64 lamps with total 4x18W fluorescent tubes with equivalent 64 lamps with 4x8W LED tubes.

TYPE 2 INDOOR

Replacement of 11 lamps with total 4x36W fluorescent tubes with equivalent 11 lamps with 4x14.5W LED tubes.

TYPE 3 INDOOR

Replacement of 29 lamps with total 1x100W Incandescent bulbs with equivalent 29 lamps with 1x12.5W LED bulbs.