## Summary
Reference No.: 1395/City of Zrenjanin/125746/31.12.2015 – 03
Reconstruction of the old sports hall in Zrenjanin
Bill Of Quantities/Electrical Works |  |  | Objects: Medison hall and Annex
| Description |  | Amount (EUR/RSD)
C.I | Power supply, distribution cabinets and main distribution |  | 0
C.II | Lightning installations |  | 0
C.III | Connections installations for fair events |  | 0
C.IV | Power supply, distribution cabinets and main distribution of the Annex |  | 0
C.V | Electrical installations of the Annex |  | 0
C.VI | Fire fighting equipment |  | 0
|  | TOTAL | 0
Tenderer:
Date:
Signature:

## C.I Power supply and distrib.
Part: 1/5
Bill Of Quantities/Electrical Works/Power supply, distribution cabinets and main distribution
pos. | POSITION DESCRIPTION | unit of measure | quantity | price per unit (EUR/RSD) | total (EUR/RSD)
C.I | POWER SUPPLY, DISTRIBUTION CABINETS AND MAIN DISTRIBUTION
1 | Shutting down, disconnecting and removal, taking out and handing over the existing independent main distribution cabinet of tin construction to the investor (MDC), of dimensions 1200x550x2000mm, for the power supply of the hall. | set | 1 |  | 0
2 | Distribution cabinet of network power supply (DC) of tin construction, with level of protection IP 54, for power supply of sub distribution cabinets, workshop fully completed, tested and with the following embedded equipment:
1 piece three way switch type AS 630 of rated power 630A for fixed installation, taken from MDC (previous position) which is being removed.
3 pieces Power reducer 400/5A for installation on a rail, "Schneider" or equivalent
1 piece Three way fuse holder STI 25/6A gG, "Schneider" or equivalent
1 piece Multimeter PM-500, "Schneider" or equivalent
1 piece Three way fuse switch ISFT 160/160A gG, "Schneider" or equivalent
3 pieces Three way fuse switch ISFT 160/125A gG, "Schneider" or equivalent
6 pieces Single-pole fuse holder SBI 63/16A gG, "Schneider" or equivalent
Nameplates, cable glands, terminal blocks and other material for wiring, labeling and installation.
|  | set | 1 |  | 0
3 | Continuation of the existing power cables type 2xPP00 A-Y 4x150, with a 3m long cable of the same type, and suitable cable connectors. Induction into a new DC, processing the ends and connecting. | set | 1 |  | 0
4 | Disconnecting and relocation of the existing sub distribution cabinet with ports (DC-P, dimensions 600x800x200mm), from the current position to the part of the hall designed for distribution cabinets, a set with the necessary installation material. | set | 1 |  | 0
5 | Standard cable trays of perforated galvanized steel sheet, PNK 300 with caps PK 300, a set with brackets and elements for connecting, route diversion and installation. | m | 6 |  | 0
6 | Power cables type PP00-Y, from the new distribution cabinet DC to the sub distribution cabinets in the room for distribution cabinets placed on already prepared routes of cable trays. Processing the ends and connecting.
| PP00 4x95 + P-Y 1x50 | m | 3 |  | 0
| PP00-Y 5x25 | m | 6 |  | 0
| PP00-Y 5x6 | m | 6 |  | 0
| PP00-Y 5x4 | m | 5 |  | 0
7 | Preparatory final works, the expenses of material purchase and transport. | circa | 1 |  | 0
8 | Inspection and testing, issuing the minutes of the expert report, connecting to power. | circa | 1 |  | 0
| TOTAL C.I - POWER SUPPLY: |  |  |  | 0

## C.II Lightning installation
Part 2/5
Bill Of Quantities/Electrical Works/Lightning installation
pos. | POSITION DESCRIPTION | unit of measure | quantity | price per unit (EUR/RSD) | total (EUR/RSD)
C.II | LIGHTING INSTALLATION
1 | New reflector lights type RT-3 Minel Schreder or equivalent with two metal-halide lamps per unit of 2x400W with boxes with ballast accessories. Installation on positions according to the new schedule, a set with the necessary installation material. | piece | 12 |  | 0
2 | Disconnecting and removal of the existing reflector lights type RT-3 Minel Schreder with two metal-halide lamps per unit of 2x400W the existing boxes with ballast accessories. Their cleaning and general service with the replacement of the possibly damaged parts. Re-installation on positions according to the new schedule, a set with the necessary installation material. | piece | 58 |  | 0
3 | Panic lighting with their own power source, automatic switching in case of power outage and automatic charging, autonomy 3h, a set with the necessary installation material. | piece | 4 |  | 0
4 | Standard cable trays of perforated galvanized steel sheet, PNK 100, a set with brackets and elements for connecting, route diversion and installation. | m | 180 |  | 0
5 | Installation cables type PP00-Y for lighting circuits according to the new schedule. Cables are placed for the most part on already set PNK holders, and partly on the structures on clamps.
| PP00-Y 5x2,5 | m | 130 |  | 0
| PP00-Y 3x2,5 | m | 240 |  | 0
| PP00-Y 3x1,5 | m | 140 |  | 0
6 | Replacement of cam switches in the distribution cabinet of lighting (DC-L), for the selection of lighting mode. Disconnecting and removal of the existing switches and connecting the new switches according to the new scheme. | set | 1 |  | 0
7 | Disconnecting and re-connecting the additional distribution cabinets of lighting (DC-L-A), according to the new lighting mode. | set | 3 |  | 0
8 | Distribution box with 3-4 glands, industrial design, IP 54, PVC | piece | 40 |  | 0
9 | Control measurement of the level of brightness and adjusting the slope and rotation of the reflector lamps, according to the data from the measurements of the lamps supplier. | circa | 1 |  | 0
10 | Preparatory final works, the expenses of material purchase and transport. | circa | 1 |  | 0
11 | Inspection and testing of electrical installations of the court lighting, measuring the brightness levels of provided lighting modes, by an authorized organization, with the issue of minutes of the expert report. | circa | 1 |  | 0
| TOTAL C.II - LIGHTNING INSTALLATION: |  |  |  | 0

## C.III Connections installation
Part 3/5
Bill Of Quantities/Electrical Works/Connections installations for fair events
pos. | POSITION DESCRIPTION | unit of measure | quantity | price per unit (EUR/RSD) | total (EUR/RSD)
C.III | CONNECTIONS INSTALLATIONS FOR FAIR EVENTS
1 | Cabal canal units with PVC pipes for mechanical protection of cables conducted in the floor.
| PVC pipes Ø 36mm in the floor. | m | 160 |  | 0
| PVC pipes Ø 29mm in the floor. | m | 160 |  | 0
2 | Standard cable trays of perforated galvanized steel sheet, PNK 100, a set with brackets and elements for connecting, route diversion and installation. | m | 60 |  | 0
3 | Floor terminal boxes, with underfloor housing for the installation of underfloor boxes. Underfloor box for installation in concrete screed or space under parquet of 90 mm height. There are 2 three way modular jacks integrated in the box, 3x16A, 400/230V, 50Hz and 2 single-phase sockets 2M, 16A, 230V, 50Hz. | set | 25 |  | 0
4 | Installation cables type PP00-Y for electrical circles of connections for fair events. Cables are placed for the most part on already set PNK holders, and partly through pre-set cable canals in the floor.
| PP00-Y 5x2,5 | m | 230 |  | 0
| PP00-Y 3x2,5 | m | 230 |  | 0
5 | Preparatory final works, the expenses of material purchase and transport. | circa | 1 |  | 0
6 | Inspection and testing, issuing the minutes of the expert report, connecting to power. | circa | 1 |  | 0
| TOTAL C.III - CONNECTIONS INSTALLATIONS: |  |  |  | 0

## C.IV Power supply of Annex
Part 4/5
Bill Of Quantities/Electrical Works/Power supply, distribution cabinets and main distribution of the Annex
pos. | POSITION DESCRIPTION | unit of measure | quantity | price per unit (EUR/RSD) | total (EUR/RSD)
C.IV | POWER SUPPLY, DISTRIBUTION CABINETS AND MAIN DISTRIBUTION OF THE ANNEX
1 | Shutting down, disconnecting and removal of the existing distribution cabinet of the annex (DC-A) from the existing technical room. Detailed inspection, cleaning, partial scheming and changes in marking of some circuit fuses according to their new purpose. Its reinstallation on the wall in the new technical room of the adapted annex. | set | 1 |  | 0
2 | Continuation of the existing power cable type PP00-Y 5x25, with a 15m long cable of the same type, and a suitable cable connector. Induction into DC, processing the ends and connecting. | set | 1 |  | 0
3 | Disconnecting and removal of the existing dilapidated lamps and installation equipment from the rooms of the annex under adaptation. | circa | 1 |  | 0
4 | Preparatory final works, the expenses of material purchase and transport. | circa | 1 |  | 0
5 | Inspection and testing, issuing the minutes of the expert report, connecting to power. | circa | 1 |  | 0
| TOTAL C.IV - POWER SUPPLY - ANNEX: |  |  |  | 0

## C.V - Electrical inst. of Annex
Part 5/5
Bill Of Quantities/Electrical Works/Electrical installations of the Annex
pos. | POSITION DESCRIPTION | unit of measure | quantity | price per unit (EUR/RSD) | total (EUR/RSD)
C.V | ELECTRICAL INSTALLATIONS OF THE ANNEX
1 | Installation cables for the installation of general lighting, panic lighting, general purpose jacks and fixed ports in the adapted rooms of the annex. The cables are set in the wall under plaster, and partly through protective tubes.
| PP00 2x1,5 | m | 20 |  | 0
| PP00-Y 3x1,5 | m | 190 |  | 0
| PP00-Y 4x1,5 | m | 15 |  | 0
| PP00-Y 3x2,5 | m | 80 |  | 0
| PP00-Y 5x2,5 | m | 15 |  | 0
2 | Delivery and installation of luminaires similar to the following types, a set with control gear, light sources and installation accessories:
| Type S1, surface mounted fluorescent light 2x36W with ballast accessories in dual conjuction and light resources, protection degree IP 66, with accessories for ceiling mounting, similar to type TITAN, BFN T 236, "Buck" or equivalent. | piece | 6 |  | 0
| Type S2, surface mounted compact fluorescent ceiling light with an opal cap and two compact fluorescent lightbulbs 18W, IP 54, with installation accessories on wall or ceiling. | piece | 15 |  | 0
3 | Panic lighting with their own power source, automatic switching in case of power outage and automatic charging, autonomy 3h, a set with the necessary installation material. | piece | 3 |  | 0
4 | Delivery, installation and connection of the SOS call system with 1 call unit, 1 disassemble unit and 2 control units. The system consists of: 1 piece - power unit 1 piece - call unit with a pull SOS button, wall mounting 1 piece - control unit, wall mounting 1 piece - disassemble unit, wall mounting 1 piece - a device for sound-light indication, wall mounting All in a set with all the connecting and installation material and accessories. | set | 2 |  | 0
5 | Delivery and setting of installation accessories:
| Single-pole installation switch, 10 A, IP54, PVC. | piece | 19 |  | 0
| Double-pole installation switch, 16 A with a signal light, IP54, PVC. | piece | 2 |  | 0
| Single-phase shockproof socket, 1x16 A industrial design, IP54, PVC. | piece | 8 |  | 0
| Three-phase shockproof socket, 3x16 A industrial design, IP54, PVC. | piece | 2 |  | 0
6 | Preparatory final works, the expenses of material purchase and transport. | circa | 1 |  | 0
7 | Inspection and testing of electrical installations of the court lighting, measuring the lighting levels of provided lighting regimes, by an authorized organization, with the issue of minutes of the expert report. | circa | 1 |  | 0
| TOTAL C.V - ELECTRICAL INST. - ANNEX: |  |  |  | 0

## C.VI - Fire fighting equipment
Part 5/5
Bill Of Quantities/Electrical Works/Electrical installations of the Annex
pos. | POSITION DESCRIPTION | unit of measure | quantity | price per unit (EUR/RSD) | total (EUR/RSD)
C.VI | FIRE FIGHTING EQUIPMENT
1 | Fire extinguisher type S-9 | piece | 8 |  | 0
2 | Fire extinguisher type CO2-5 | piece | 2 |  | 0
3 | Information plates with evacuation procedure in case of fire | piece | 10 |  | 0
| TOTAL C.VI - FIRE FIGHTING EQUIPMENT: |  |  |  | 0